Aluminum Stranded Conductor and

## Aluminum Stranded Conductor Steel-reinforced

The product is used in the field of aerial power line.

- Manufacturing Standards:

The standard is IEC207—1966, GB1179-83 which is aqural  to IEC209—1966.

- Type & Specification:

a. Refer to table 1 about the type of cable:

Table 1

| Type | Name |
| --- | --- |
| LJ | Aluminum Stranded Conductor |
| LGJ | Aluminum Stranded Conductors Steel-reinforced |
| LGJF | Corrosion-proof Aluminum Stranded Conductors Steel-reinforced |

b. Specification of cable is stipulated in table 2 and table 3.

Aluminum Stranded Conductor                                                Table 2

| Nominal Cross-sectional Area mm2 | Construction （No./Dia） mm | Outer Dia. mm | D.C .Resistance at 20℃ (no more than) Ω/km | Calculated Breaking Load N | Calculated Weight kg/km | Delivery Length （no less than） m | Continuous Carrying Capacity A |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 16 25 35 | 7/1.70 7/2.15 7/2.50 | 5.10 6.45 7.50 | 1.802 1.127 0.8332 | 2840 4355 5760 | 44 70 94 | 4000 3000 2000 | 111 147 180 |
| 50 70 95 | 7/3.00 7/3.60 7/4.16 | 9.00 10.80 12.48 | 0.5786 0.4018 0.3009 | 7930 10950 14450 | 136 195 261 | 1500 1250 1000 | 227 284 338 |
| 120 150 185 | 19/2.85 19/3.15 19/3.50 | 14.25 15.75 17.50 | 0.2373 0.1943 0.1574 | 19420 23310 28440 | 334 407 503 | 1500 1250 1000 | 390 454 518 |
| 210 240 300 | 19/3.75 19/4.00 37/3.20 | 18.75 20.00 22.40 | 0.1371 0.1205 0.09689 | 32260 36260 46850 | 577 657 820 | 1000 1000 1000 | 575 610 707 |
| 400 500 630 | 37/3.70 37/4.16 61/3.63 | 25.90 29.12 32.67 | 0.07247 0.05733 0.04577 | 61150 76370 91940 | 1097 1387 1744 | 1000 1000 800 | 851 982 1140 |
| 800 | 61/4.10 | 36.90 | 0.03588 | 115900 | 2225 | 800 | 1340 |

Aluminum Stranded Conductors Steel-reinforced

| Nominal Cross-sectional Area mm2 | Construction （No./Dia） mm |  | Outer Dia. mm | 2D.C. Resistance at 0℃ (no more than) Ω/km | Calculated Breaking Load N | Calculated Weight kg/km | Delivery Length (no less than) m | Continuous Carrying Capacity A |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Al. | St. |  |  |  |  |  |  |
| 10/2 16/3 25/4 35/6 | 6/1.50 6/1.85 6/2.32 6/2.72 | 1/1.50 1/1.85 1/2.32 1/2.72 | 4.50 5.55 6.96 8.16 | 2.706 1.779 1.131 0.8230 | 4120 6130 9290 12630 | 43 65 103 141 | 3000 3000 3000 3000 | 87 110 125 145 |
| 50/8 50/30 70/10 70/40 | 6/3.20 12/2.32 6/3.80 12/2.72 | 1/3.20 7/2.32 1/3.80 7/2.72 | 9.60 11.60 11.40 13.60 | 0.5946 0.5692 0.4217 0.4141 | 16870 42620 23390 58300 | 195 372 275 511 | 2000 3000 2000 2000 | 212 250 255 340 |
| 95/15 95/20 95/55 | 26/2.15 7/4.16 12/3.20 | 7/1.67 7/1.85 7/3.20 | 13.61 13.87 16.00 | 0.3058 0.3019 0.2992 | 35000 37200 78110 | 381 409 708 | 2000 2000 2000 | 350 360 420 |
| 120/7 120/20 120/25 120/70 | 18/2.90 26/2.38 7/4.72 12/3.60 | 1/2.90 7/1.85 7/2.10 7/3.60 | 14.50 15.07 15.74 18.00 | 0.2422 0.2496 0.2345 0.2364 | 27570 41000 47880 98370 | 379 467 527 896 | 2000 2000 2000 2000 | 380 390 400 505 |
| 150/8 150/20 150/25 150/35 | 18/3.20 24/2.78 26/2.70 30/2.50 | 1/3.20 7/1.85 7/2.10 7/2.50 | 16.00 16.67 17.10 17.50 | 0.1989 0.1980 0.1939 0.1962 | 32860 46630 54110 65020 | 461 549 601 676 | 2000 2000 2000 2000 | 442 450 470 500 |
| 185/10 185/25 185/30 185/45 | 18/3.60 24/3.15 26/2.98 30/2.80 | 1/3.60 7/2.10 7/2.32 7/2.80 | 18.00 18.90 18.88 19.60 | 0.1572 0.1542 0.1592 0.1564 | 40880 59420 64320 80190 | 584 706 733 848 | 2000 2000 2000 2000 | 497 525 525 522 |
| 210/10 210/25 210/35 210/50 | 18/3.80 24/3.33 26/3.22 30/2.98 | 1/3.80 7/2.22 7/2.50 7/2.98 | 19.00 19.98 20.38 20.86 | 0.1411 0.1380 0.1363 0.1381 | 45140 65990 74250 90830 | 651 789 854 961 | 2000 2000 2000 2000 | 523 560 590 600 |
| 240/30 240/40 240/55 | 24/3.60 26/3.42 30/3.20 | 7/2.40 7/2.66 7/3.20 | 21.60 21.66 22.40 | 0.1181 0.1209 0.1198 | 75620 83370 102100 | 922 964 1108 | 2000 2000 2000 | 610 610 640 |
| 300/15 300/20 300/25 | 42/3.00 45/2.93 48/2.85 | 7/1.67 7/1.95 7/2.22 | 23.01 23.43 23.76 | 0.09724 0.09520 0.09433 | 68060 75680 83410 | 940 1002 1058 | 2000 2000 2000 | 650 655 690 |
| 300/40 300/50 300/70 | 24/3.99 26/3.83 30/3.60 | 7/2.66 7/2.98 7/3.60 | 23.94 24.26 25.20 | 0.09614 0.09636 0.09463 | 92220 103400 128000 | 1133 1210 1402 | 2000 2000 2000 | 705 725 740 |
| 400/20 400/25 400/35 | 42/3.51 45/3.33 48/3.22 | 7/1.95 7/2.22 7/2.50 | 26.91 26.64 26.82 | 0.07104 0.07370 0.07389 | 88850 95940 103900 | 1286 1295 1349 | 1500 1500 1500 | 800 800 810 |
| 400/50 400/65 400/95 | 54/3.07 26/4.42 30/4.16 | 7/3.07 7/3.44 19/2.50 | 27.63 28.00 29.14 | 0.07232 0.07236 0.07087 | 123400 135200 171300 | 1511 1611 1860 | 1500 1500 1500 | 815 850 873 |
| 500/35 500/45 500/65 | 45/3.75 48/3.60 54/3.44 | 7/2.50 7/2.80 7/3.44 | 30.00 30.00 30.96 | 0.05812 0.05912 0.05760 | 119500 128100 154000 | 1642 1688 1897 | 1500 1500 1500 | 920 920 935 |
| 630/45 630/55 630/80 | 45/4.20 48/4.12 54/3.87 | 7/2.80 7/3.20 19/2.32 | 33.60 34.32 34.82 | 0.04633 0.04514 0.04551 | 148700 164400 192900 | 2060 2209 2388 | 1200 1200 1200 | 1025 1060 1120 |
| 800/55 800/70 800/100 | 45/4.80 48/4.63 54/4.33 | 7/3.20 7/3.60 19/2.60 | 38.40 38.58 38.98 | 0.03547 0.03574 0.03635 | 191500 207000 241100 | 2690 2791 2991 | 1000 1000 1000 | 1220 1223 1240 |

3.  Main Mechanical Performance of Cable:

- Refer to table 4 about the mechanical performance of round aluminum wire.

- The mechanical property of galvanized steel wire and the technical requirement of zinc coating. (see Table 5)

Table4

| Nominal Diameter mm | Min. Tensile Strength |  |  |  | Max. Resistivity at 20℃ Ωmm2/m | Wrapping Test |
| --- | --- | --- | --- | --- | --- | --- |
|  | Before Stranding |  | After Stranding |  |  | Wind test sample at round rod whose diameter is equal to that of sample eight turns, then unwind six turns, then wind sample at the rod tightly again. There should be no breaking on aluminum stranded conductors when checked by visual examination. |
|  | N/mm2 | kgf/mm2 | N/mm2 | kgf/mm2 |  |  |
| 1.25 | 200 | 20.4 | 190 | 19.4 | 0.028264 |  |
| 1.26～1.50 | 193 | 19.7 | 183 | 18.7 |  |  |
| 1.51～1.75 | 188 | 19.2 | 178 | 18.2 |  |  |
| 1.76～2.00 | 184 | 18.8 | 176 | 17.9 |  |  |
| 2.01～2.25 | 180 | 18.4 | 172 | 17.5 |  |  |
| 2.26～2.50 | 176 | 18.0 | 168 | 17.1 |  |  |
| 2.51～2.75 | 173 | 17.6 | 164 | 16.7 |  |  |
| 2.76～3.00 | 169 | 17.2 | 160 | 16.3 |  |  |
| 3.01～3.25 | 166 | 16.9 | 157 | 16.0 |  |  |
| 3.26～3.50 | 164 | 16.7 | 156 | 15.9 |  |  |
| 3.51～3.75 | 162 | 16.5 | 154 | 15.7 |  |  |
| 3.76～4.20 | 160 | 16.3 | 152 | 15.5 |  |  |
| 4.26～5.00 | 159 | 16.2 | 151 | 15.4 |  |  |

Table 5

| Nominal Diameter mm | Min. Stress at 1％ N/mm2 | Min. Tensile Strength N/mm2 |  | Min. Weight of Zinc Coating g/mm2 | No. of Immersion in 1 minute (No less than) | Adhesion of Coating |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Before Stranding | After Stranding |  |  | Dia. Of Test Rod mm | Wrapping |
| 1.25～1.50 | 1172 | 1310 | 1244 | 183 | 2 | 4d | - Wind 8 turns tightly. (2) Winding result: No crack on coating dropped off when rubbed by finger. |
| 1.51～1.75 | 1172 | 1310 | 1244 | 198 | 2 |  |  |
| 1.76～2.25 | 1172 | 1310 | 1244 | 214 | 2.5 |  |  |
| 2.26～2.75 | 1138 | 1310 | 1244 | 229 | 3 |  |  |
| 2.76～3.00 | 1138 | 1310 | 1244 | 244 | 3.5 |  |  |
| 3.01～3.50 | 1103 | 1310 | 1244 | 244 | 3.5 |  |  |
| 3.51～3.80 | 1103 | 1310 | 1244 | 259 | 4 | 5d |  |

- Construction of the Cable:

  - Aluminum stranded conductors and thermal resistant aluminum alloy stranded conductors.

  - Aluminum stranded conductors steel-reinforced and steel-reinforced aluminum alloy conductors.

Thermal Resistant Aluminum Alloy Stranded Conductor and Thermal Resistant Aluminum Alloy Stranded Conductor Steel-reinforced

- Manufacturing Standard:

Factory standard

2.  Uses and Characteristics:

The product is used in aerial transmission line. Max. continuous operating temperature can be 150℃. The transmission capacity of this product increases 60%.

- Properties:

  - Relative conductance: 58%IACS（Max. resistivity at 20℃: 0.029726Ω·mm2/m）

  - After heating to 230℃ for 1h, and cooling to room temperature, the tensile strength remained should not less than 90%.

  - Linear expansion coefficient is  0.000023  1/℃.

  - Temperature coefficient of resistance is 0.0039  1/℃.

4.  Type of Products:

1．NR LH 58J

Stranded conductor

Relative conductance: 58%

Aluminum alloy

Thermal resistant

2．NR LH 58GJ

Steel-reinforced stranded conductor

Relative conductance: 58%

Aluminum alloy

Thermal resistant

- Specification:

a.  thermal resistant aluminum alloy stranded conductor

Table  6

| Nominal Cross-section mm2 | Construction(No./Dia.) mm | Calculated Cross-section mm2 | Overall Diameter mm | Max. D.C. Resistance at 20℃ Ω/km | Calculated Breaking Load N | Calculated Weight kg/km | Min. Delivery Length m |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 35 | 7/2.50 | 34.36 | 7.50 | 0.8763 | 5125 | 94.2 | 2000 |
| 50 | 7/3.00 | 49.48 | 9.00 | 0.6085 | 7380 | 135.7 | 1500 |
| 70 | 7/3.60 | 71.25 | 10.80 | 0.4226 | 10289 | 195.4 | 1250 |
| 95 | 7/4.16 | 95.14 | 12.48 | 0.3165 | 13287 | 260.9 | 1000 |
| 120 | 19/2.85 | 121.21 | 14.25 | 0.2496 | 18079 | 334.0 | 1500 |
| 150 | 19/3.15 | 148.07 | 15.75 | 0.2043 | 21381 | 408.0 | 1250 |
| 185 | 19/3.50 | 182.80 | 17.50 | 0.1655 | 26396 | 503.7 | 1000 |
| 210 | 19/3.75 | 209.85 | 18.75 | 0.1442 | 30302 | 578.2 | 1000 |
| 240 | 19/4.00 | 238.76 | 20.00 | 0.1267 | 33343 | 657.9 | 1000 |
| 300 | 37/3.20 | 297.57 | 22.40 | 0.1019 | 42969 | 821.6 | 1000 |
| 400 | 37/3.70 | 397.83 | 25.90 | 0.07622 | 57447 | 1098.5 | 1000 |
| 500 | 37/4.16 | 502.90 | 29.12 | 0.06030 | 70230 | 1388.6 | 1000 |
| 630 | 61/3.63 | 631.30 | 32.67 | 0.04803 | 86362 | 1746.8 | 800 |
| 800 | 61/4.10 | 805.36 | 36.90 | 0.03765 | 106549 | 2228.4 | 800 |

b.  thermal resistant aluminum alloy stranded conductor steel-reinforced

Table 7

| Nominal Cross- Section mm2 | Construction (No./Dia.) mm |  | Calculated Cross-section mm2 |  |  | Overall Diameter mm | Max. D.C. Resistance at 20℃ Ω/km | Calculated Breaking Load N | Calculated Weight kg/km | Min. Delivery Length m |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Al. | St. | Al. | St. | Total |  |  |  |  |  |
| 240/30 | 24/3.60 | 7/2.40 | 244.29 | 31.67 | 275.06 | 21.60 | 0.1242 | 73170 | 923 | 2000 |
| 240/40 | 26/3.42 | 7/2.66 | 238.85 | 38.90 | 277.75 | 21.66 | 0.1271 | 80570 | 965 | 2000 |
| 240/55 | 30/3.20 | 7/3.20 | 241.27 | 56.30 | 297.57 | 22.40 | 0.1260 | 98770 | 1109 | 2000 |
| 300/15 | 42/3.00 | 7/1.67 | 296.88 | 15.33 | 312.21 | 23.01 | 0.1023 | 64580 | 941 | 2000 |
| 300/20 | 45/2.93 | 7/1.95 | 303.42 | 20.91 | 324.33 | 23.43 | 0.1001 | 72140 | 1003 | 2000 |
| 300/25 | 48/2.85 | 7/2.22 | 306.21 | 27.10 | 333.31 | 23.76 | 0.0992 | 79840 | 1060 | 2000 |
| 300/40 | 24/3.99 | 7/2.65 | 300.09 | 38.90 | 338.99 | 23.94 | 0.1011 | 89880 | 1134 | 2000 |
| 300/50 | 26/3.83 | 7/2.98 | 299.54 | 48.82 | 348.36 | 24.26 | 0.1013 | 101100 | 1211 | 2000 |
| 300/70 | 30/3.60 | 7/3.60 | 305.36 | 71.25 | 376.61 | 25.20 | 0.09953 | 125000 | 1403 | 2000 |
| 400/20 | 42/3.51 | 7/1.95 | 406.40 | 20.91 | 427.31 | 26.91 | 0.07471 | 86280 | 1287 | 1500 |
| 400/25 | 45/3.33 | 7/2.22 | 391.91 | 27.10 | 419.01 | 26.64 | 0.07751 | 91330 | 1297 | 1500 |
| 400/35 | 48/3.22 | 7/2.50 | 390.88 | 34.36 | 425.24 | 26.82 | 0.07772 | 98520 | 1351 | 1500 |
| 400/50 | 54/3.07 | 7/3.07 | 399.73 | 51.82 | 451.55 | 27.63 | 0.07606 | 117920 | 1513 | 1500 |
| 400/65 | 26/4.42 | 7/3.44 | 398.94 | 65.06 | 464.00 | 28.00 | 0.07610 | 130400 | 1612 | 1500 |
| 400/95 | 30/4.16 | 19/2.50 | 407.75 | 93.27 | 501.02 | 29.14 | 0.07454 | 166100 | 1961 | 1500 |
| 500/35 | 45/3.75 | 7/2.50 | 497.01 | 34.36 | 531.37 | 30.00 | 0.06112 | 114700 | 1644 | 1500 |
| 500/45 | 48/3.60 | 7/2.80 | 488.58 | 43.10 | 531.68 | 30.00 | 0.06218 | 123300 | 1690 | 1500 |
| 500/65 | 54/3.44 | 7/3.44 | 501.88 | 65.06 | 566.94 | 30.96 | 0.0606 | 148000 | 1899 | 1500 |
| 630/45 | 45/4.20 | 7/2.80 | 623.45 | 43.10 | 666.55 | 33.60 | 0.04873 | 140700 | 2061 | 1200 |
| 630/55 | 48/4.12 | 7/3.20 | 639.92 | 56.30 | 696.22 | 34.32 | 0.04747 | 156200 | 2210 | 1200 |
| 630/80 | 54/3.87 | 19/2.32 | 635.19 | 80.32 | 715.51 | 34.82 | 0.0479 | 187800 | 2190 | 1200 |
| 800/55 | 45/4.80 | 7/3.20 | 814.30 | 56.30 | 870.60 | 38.40 | 0.03731 | 181800 | 2691 | 1000 |
| 800/70 | 48/4.63 | 7/3.60 | 808.15 | 71.25 | 379.40 | 33.53 | 0.03759 | 197400 | 2793 | 1000 |
| 800/100 | 54/4.33 | 19/2.60 | 795.17 | 100.88 | 896.05 | 38.98 | 0.0383 | 231600 | 2995 | 1000 |
| 1440/120 | 84/4.67 | 19/2.80 | 1438.81 | 116.99 | 1555.80 | 51.36 | 0.0213 | 344500 | 4928 | 700 |

- Material

  - Thermal resistant aluminum alloy round wire should be in accordance with the standard Q/09TDL029-1999 Thermal Resistant Aluminum Alloy Round Wire of Relative Conductance 58% IACS.

  - Galvanized steel wire should be in accordance with the standard GB3428-82 Galvanized Steel Wire which is used in Aluminum Stranded Conductors Steel-reinforced.

Hard Copper Stranded Conductor

    - Manufacturing Standard: factory standard

    - Uses: The product is used in aerial power line and power system of electrical railway.

    - Name and Manufacturing Range:

Name: Hard Copper Stranded Conductor

Type: TJ

Manufacturing Range: 16-500mm2

4.  Main Properties of Round Copper Single Wire (see Table 8)

Table 8

| Dia. Of Single Wire mm |  | Cross-section of Conductor mm2 | Tensile Strength N/mm2 |  | Conductor Resistivity at 20℃ Ω·mm2/m | Weight kg/km |
| --- | --- | --- | --- | --- | --- | --- |
| Normal Value | Tolerance |  | Min. Value before Stranding | Min. Value after Stranding |  |  |
| 1.35 | ±0.03 | 1.43 | 422 | 392 | 0.01796 | 12.7 |
| 1.50 |  | 1.77 |  |  |  | 15.3 |
| 1.75 |  | 2.41 |  |  |  | 21.5 |
| 2.00 |  | 3.14 |  |  | 0.01777 | 28.0 |
| 2.25 |  | 3.98 |  |  |  | 35.4 |
| 2.50 |  | 4.91 |  |  |  | 43.7 |
| 2.70 |  | 5.94 |  |  |  | 52.9 |
| 3.00 |  | 7.07 |  |  |  | 62.9 |
| 3.25 | ±0.04 | 8.30 |  |  |  | 73.8 |
| Note: 1. The diameter is allowed to have a middle value. Its deviation is allowed one of the next bigger diameter. 2. Resistivity of the conductor at 20℃ shall be selected 0.01796Ω·mm2/m, if the normal diameter is less than 2.00mm. |  |  |  |  |  |  |

5. The Construction

6.  Specification, Construction and Technical Data. (see Table 9)

Table  9

| No. | Nominal Cross-section mm2 | Single Wire |  | Overall Diameter of the Strand mm | Calculated Breaking Load KN | Conductor D.C. Resistance at 20℃ Ω·/km | Continuous Carrying Capacity A | Calculated Weight kg/km |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | No. | Dia. mm |  |  |  |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| 1 | 10 | 7 | 1.35 | 4.1 | 4.02 | 1.8156 | 90 | 90 |
| 2 | 16 | 7 | 1.70 | 5.1 | 6.37 | 1.1450 | 125 | 143 |
| 3 | 25 | 7 | 2.10 | 6.3 | 9.72 | 0.7424 | 160 | 218 |
| 4 | 35 | 7 | 2.50 | 7.5 | 13.77 | 0.5238 | 200 | 310 |
| 5 | 50 | 7 | 3.00 | 9.0 | 19.84 | 0.3638 | 250 | 446 |
| 6 | 50 | 19 | 1.80 | 9.0 | 19.38 | 0.3781 | 250 | 437 |
| 7 | 70 | 19 | 2.10 | 10.5 | 26.38 | 0.2747 | 310 | 596 |
| 8 | 95 | 19 | 2.50 | 12.5 | 37.39 | 0.1939 | 380 | 845 |
| 9 | 120 | 19 | 2.80 | 14.0 | 46.90 | 0.1546 | 440 | 1060 |
| 10 | 127 | 19 | 2.92 | 14.6 | 51.00 | 0.1422 | 470 | 1163 |
| 11 | 150 | 37 | 2.25 | 15.8 | 58.98 | 0.1232 | 510 | 1337 |
| 12 | 185 | 37 | 2.50 | 17.5 | 72.81 | 0.09981 | 585 | 1649 |
| 13 | 240 | 61 | 2.25 | 20.3 | 97.23 | 0.07490 | 700 | 2209 |
| 14 | 300 | 61 | 2.50 | 22.5 | 120.04 | 0.06067 | 800 | 2725 |
| 15 | 400 | 61 | 2.89 | 26.0 | 160.42 | 0.04540 | 960 | 3640 |
| 16 | 500 | 61 | 3.23 | 29.1 | 200.38 | 0.03635 | 1110 | 4545 |
| Note: 1. The weight of stranded conductor is calculated with the density 8.9kg/dm3 and average lay ratio. 2. Refer to the line, the wind speed is 0.6m/s, the ambient temperature is 35℃, max. temperature of aerial transmission strand is 70℃, 60Hz and below. In the special laying situation of static air, the capacity shall reduce about 30% in average. |  |  |  |  |  |  |  |  |

- Delivery Length:

  - the delivery length of stranded conductors shall be as stipulated in the tables. The allowed tolerance for delivery length of any strands is within 5% of the total length signed in the contract, the length for each short strand shall be not less than 1/3 of the standard delivery one.

The delivery length can be decided through negotiation by both parties.

  - The strands shall be delivered in drum and packed carefully. The short strands shall be delivered in coiling and tied up at least three points and packed carefully.

- Ordering Method:

Please indicate the type, size, number and product standard when ordering. For example, if ordering 20T steel-reinforced aluminum stranded conductor with a cross-sectional area of 50/8mm2 can be indicated as: LGJ-50/8mm2 20T GB1179-83.