Plastic Insulated Control Cable

The products are used as connection wire in distribution eqipment, e.g. electrical appliances and instruments with the A.C. Rated voltages 450/750V PVC insulated control cable, Rated voltage 0.6/1kV XLPE insulated control cable.

- Standards:

GB9330-88 Plastic Insulated Control Cable  was made with reference to IEC 227.5-79 XLPE insulated cable refer to GB12706-91 Rated Voltage up to 35kV plastic insulated power cable.

- Application and Specification:

  - The permissible continuous conductor operating temperature: PVC insulated cable is 70℃，XLPE insulated cable is 90℃.

  - The installation temperature should not be lower than 0℃ during installation.

  - Permissible bending radius of cable.

i. for unarmored cables: no less than 6 times of overall diameter of cable.

ii. for armored or copper tape screened cables: no less than 12 times of overall diameter of cable.

iii. for screened flexible cables: no less than 6 times of overall diameter of cable.

Table: 1

| Tyep | Name | Main Applications |
| --- | --- | --- |
| KVV （KYJV） | Copper conductor PVC (XLPE) insulated PVC sheathed control cable | Use in fixed places such as indoors, trenches, conduits, etc |
| KVVP （KYJVP） | Copper conductor PVC (XLPE) insulated PVC sheathed woven shield control cable | Use in screened and fixed places such as indoors, trenches, conduits, etc. |
| KVVP2 （KYJVP2） | Copper conductor PVC (XLPE) insulated PVC sheathed copper tape shieldcontrol cable | Use in screened and fixed places such as indoors, trenches, conduits,etc |
| KVV22 （KYJV22） | Copper conductor PVC (XLPE) insulated PVC sheathed steel tape armored control cable | Use in fixed places eg. Indoors, trenches, conduits, direct burial etc. with very high mechanical stresses |
| KVVP22 （KYJVP22） | Copper conductor PVC (XLPE) insulated PVC sheathed woven shield steel tape armored control cable | Use in screened and fixed places, eg. Indoors, trenches, conduits, direct burial etc. with very high mechanical stresses. |
| KVVP2-22 （KYJVP2-22） | Copper conductor PVC (XLPE) insulated PVC sheathed copper tape shield steel tape armored control cable | Use in screened and fixed places, eg. Indoors, trenches, conduits, direct burial etc. with very high mechanical stresses. |
| KVV32 （KYJV32） | Copper conductor PVC (XLPE) insulated PVC sheathed thin steel wire armored control cable | Use in fixed places, eg. Indoors, trenches, conduits, shafts, etc. with very high mechanical stresses. |
| KVVR | Copper conductor PVC insulated PVC sheathed control flexible cable | Use indoors, require a flexible place in moving |
| KVVRP | Copper conductor PVC insulated PVC sheathed woven shield control flexible cable | Use indoors, require a flexible and screened place in moving |

Note:

Our company can also produce flame-retardant, fire-resistant, anti-termite, low smoke and non-halogen cables respectively according to the requirements of customers.

eg.: for flame-retardant cables, the writing “ZRA-”, “ZRB-”, “ZRC-” is added respectively;

for fire-resistant cables, the writing “NH-” is added;

for low smoke and non-halogen cables, the writing “DWZR-” is added;

for low smoke and low-halogen cables, the writing “DDZR-” is added.

Type and Specification:

  - Refer to table 1 about the cable type.

  - Refer to table 2, 3 about the cable specification.

PVC insulated control cable                                                  Table 2

| Type | Rated Voltage V | Nominal Cross-section of Cconductor mm2 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 0.5 | 0.75 | 1.0 | 1.5 | 2.5 | 4 | 6 | 10 |
|  |  | No. of Cores |  |  |  |  |  |  |  |
| KVV KVVP | 450/750 | - | 2~61 |  |  |  | 2~14 |  | 2~10 |
| KVVP2 |  | - | 4~61 |  |  |  | 4~14 |  | 4~10 |
| KVV22 |  | - | 7~61 |  |  | 4~61 | 4~14 |  | 4~10 |
| KVV32 |  | - | 19~61 |  | 7~61 |  | 4~14 |  | 4~10 |
| KVVR |  | 4~61 |  |  |  |  | - |  | - |
| KVVRP |  | 4~61 |  |  | 4~48 |  | - |  | - |

XLPE insulated control cable                                                 Table 3

| Type | Rated Voltage V | Nominal Cross-section of Conductor mm2 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1.5 | 2.5 | 4 |  | 6 | 10 |
|  |  | No. of Cores |  |  |  |  |  |
| KYJV | 600/1000 | 2-61 |  |  | 2-14 |  | 2-10 |
| KYJV22 |  | 4-61 |  |  | 4-14 |  | 2-10 |
| KYJV32 |  | 4-61 |  |  | 4-14 |  | 2-10 |
| KYJVP |  | 2-61 |  |  | 2-14 |  | 2-10 |
| KYJVP2 |  | 2-61 |  |  | 2-14 |  | 2-7 |
|  |  | 2-61 |  |  | 2-14 |  | 2-10 |

Table 4

| Nominal Cross-section mm2 | Resistance of Conductor at 20℃ (no more than) Ω/km | Nominal Cross-section mm2 | Resistance of Conductor at 20℃ (no more than) Ω/km |
| --- | --- | --- | --- |
| 0.75（1/0.97） 0.75（7/0.37） 1.0（1/1.13） 1.0（7/0.43） 1.5（1/1.38） 1.5（7/0.52） | 24.5 24.5 18.1 18.1 12.1 12.1 | 2.5（1/1.78） 2.5（7/0.68） 4（1/2.25） 4（7/0.85） 6（1/2.76） 6（7/1.04） 10（7/1.35） | 7.41 7.41 4.61 4.61 3.08 3.08 1.83 |

4.  Refer to table 5-11 about dimensions of the cable and fig. 1-7 about construction:

- Technical Performance:

  - Copper conductor shall comply with the requirements-copper or aluminum conductors of wire and cable for electric equirement in GB/T3956-1997.

  - The completed cable should withstand a voltage of: 3000V A.C. 50Hz for 5 minutes for PVC insualted 3500V A.C. 50Hz for 5 minutes for XLPE insulated.

  - D.C resistance of conductor should be as stipulated in Table 3.

  - After the above-mentioned voltage withstand test, the insulation resistance test for completed cable shall be conduced on a test piece of 5m long. PVC/XLPE immersing into water at 70℃, 90℃, for at least 1 hour. The value should be as stipulated in Table 5-11.

- Delivery Length:

The length of cable in every coil is 100m, in every reel no less than 100mm.

Cores up to 24: no less than 20m long short strands for delivery is permissible, but the quantity no more than 5% of the total delivery lengths.

Above 24 cores: no less than 20m long short strands for delivery is permissible, but the quantity no more than 10% of the total delivery length.

The delivery length can be decided through negotiation by both parties.

- Writing of type and size to order:

Please indicate the type, size, quantity, etc. when ordering cable.

For example: 2km 30cores 2.5mm2 copper conductor PVC insulated PVC sheathed control cable.

Please write: KVV-450/750V 30x2.5mm2, 2km GB9330-88

Type: KVV（KYJV）  Rated Voltage: 450／750V（600／1000V）                      Table 5（1）

| No. of Cores×Nominal Cross-section mm2 | Kind of Conductor | Nominal Thickness of Insulation mm | Nominal Thickness of Sheath mm | Average Outer Diameter mm |  | Min. Insulation Resistance at 70℃／90℃（PVC／XLPE） MΩ·km |  | Approx. Weight kg／km |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Lower Limit | Uppe limit |  |  |  |  |
|  |  |  |  |  |  | KVV | KYJV | KVV | KYJV |
| 4×2.5 4×4 4×4 4×6 4×6 4×10 | 2 1 2 1 2 2 | 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 1.0／0.7 | 1.2 1.5 1.5 1.5 1.5 1.5 | 10.0／9.5 11.5／11.0 12.0／11.5 12.5／12.0 13.0／12.5 16.0／14.6 | 13.0／12.5 14.0／13.5 15.0／14.5 15.0／14.5 16.5／16.0 20.0／18.6 | 0.009 0.0085 0.0077 0.0070 0.0065 0.0065 | 0.707 0.664 0.601 0.567 0.527 0.458 | 211 291 301 384 396 608 | 199 277 287 368 380 579 |
| 5×0.75 5×0.75 5×1.0 5×1.0 5×1.5 5×1.5 5×2.5 5×2.5 5×4 5×4 5×6 5×6 5×10 | 1 2 1 2 1 2 1 2 1 2 1 2 2 | 0.6／- 0.6／- 0.6／- 0.6／- 0.7／0.7 0.7／0.7 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 1.0／0.7 | 1.2 1.2 1.2 1.2 1.2 1.2 1.5 1.5 1.5 1.5 1.5 1.5 1.7 | 7.8／- 8.0／- 8.2／- 8.4／- 9.4／9.4 9.8／9.8 11.5／11.0 11.5／11.0 12.5／12.0 13.0／12.5 14.0／13.5 14.5／14.0 18.0／16.4 | 9.6／- 10.5／- 10.0／- 11.0／- 11.5／11.5 12.5／12.5 14.0／13.5 14.5／14.0 15.0／14.5 16.5／16.0 16.5／16.0 18.0／17.5 22.5／20.9 | 0.012 0.014 0.011 0.013 0.011 0.010 0.010 0.009 0.0085 0.0077 0.0070 0.0065 0.0065 | - - - - 0.948 0.863 0.785 0.707 0.664 0.601 0.567 0.527 0.458 | 119 116 129 139 170 176 259 270 349 361 464 478 757 | - - - - 162 166 244 255 332 344 444 468 723 |
| 7×0.75 7×0.75 7×1.0 7×1.0 7×1.5 7×1.5 7×2.5 7×2.5 7×4 7×4 7×6 7×6 7×10 | 1 2 1 2 1 2 1 2 1 2 1 2 2 | 0.6／- 0.6／- 0.6／- 0.6／- 0.7／0.7 0.7／0.7 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 1.0／0.7 | 1.2 1.2 1.2 1.2 1.2 1.2 1.5 1.5 1.5 1.5 1.5 1.5 1.7 | 8.4／- 8.8／- 9.0／- 9.2／- 10.0／10.0 10.5／10.5 12.5／11.9 12.5／11.9 13.5／12.9 14.0／13.4 15.0／14.4 15.5／14.9 20.0／18.2 | 10.5／- 11.0／- 11.0／- 11.5／- 12.5／12.5 13.5／13.5 15.0／14.4 16.0／15.4 16.5／15.9 17.5／16.9 18.0／17.4 19.5／18.9 24.0／22.2 | 0.012 0.014 0.011 0.013 0.011 0.010 0.010 0.009 0.0085 0.0077 0.0070 0.0065 0.0065 | - - - - 0.948 0.863 0.785 0.707 0.664 0.601 0.567 0.527 0.458 | 139 144 163 175 216 224 333 345 456 471 613 632 1007 | - - - - 212 210 312 324 432 447 585 604 957 |
| 8×0.75 | 1 | 0.6／- | 1.2 | 9.4／- | 11.5／- | 0.012 | - | 155 | - |

Type: KVV（KYJV）  Rated Voltage: 450／750V（600／1000V）                     Table 5 (2) continued

| No. of Cores× Nominal Cross-section mm2 | Kind of Conductor | Nominal Thickness of Insulation mm | Nominal Thickness of Sheath mm | Average Outer Diameter mm |  | Min. Insulation Resistance at 70℃／90℃（PVC／XLPE） MΩ·km |  | Approx. Weight kg／km |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Lower Limit | Uppe limit |  |  |  |  |
|  |  |  |  |  |  | KVV | KYJV | KVV | KYJV |
| 8×0.75 8×1.0 8×1.0 8×1.5 8×1.5 8×2.5 8×2.5 8×4 8×4 8×6 8×6 8×10 | 2 1 2 1 2 1 2 1 2 1 2 2 | 0.6／- 0.6／- 0.6／- 0.7／0.7 0.7／0.7 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 1.0／0.7 | 1.2 1.2 1.2 1.5 1.5 1.5 1.5 1.5 1.5 1.7 1.7 1.7 | 9.6／- 10.0／- 10.0／- 12.0／12.0 12.5／12.5 14.0／13.3 14.0／13.3 15.5／14.8 16.0／15.3 17.5／16.8 18.0／17.3 22.5／20.5 | 12.0／- 12.0／- 13.0／- 14.5／14.5 15.5／15.5 16.5／15.8 17.5／16.8 18.0／17.3 19.5／18.8 20.0／19.3 22.0／21.3 27.0／25.0 | 0.014 0.011 0.013 0.011 0.010 0.010 0.009 0.0085 0.0077 0.0070 0.0065 0.0065 | - - - 0.949 0.863 0.785 0.707 0.664 0.601 0.567 0.527 0.458 | 161 181 196 260 269 374 389 514 531 709 730 1141 | - - - 247 256 355 370 488 504 674 694 1084 |
| 10×0.75 10×0.75 10×1.0 10×1.0 10×1.5 10×1.5 10×2.5 10×2.5 10×4 10×4 10×6 10×6 10×10 | 1 2 1 2 1 2 1 2 1 2 1 2 2 | 0.6／- 0.6／- 0.6／- 0.6／- 0.7／0.7 0.7／0.7 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 1.0／0.7 | 1.2 1.2 1.5 1.5 1.5 1.5 1.5 1.5 1.7 1.7 1.7 1.7 1.7 | 10.5／- 10.5／- 11.5／- 12.0／- 13.5／13.5 14.0／14.0 15.5／14.7 16.0／15.2 18.0／17.2 18.5／17.7 19.5／18.7 20.5／19.7 25.5／23.1 | 12.5／- 13.5／- 14.0／- 15.0／- 16.0／16.0 17.0／17.0 18.5／17.7 19.5／18.7 20.5／19.7 22.5／21.7 22.5／21.7 25.0／24.2 30.5／28.1 | 0.012 0.014 0.011 0.013 0.011 0.010 0.010 0.009 0.0085 0.0077 0.0070 0.0065 0.0065 | - - - - 0.949 0.863 0.785 0.707 0.664 0.601 0.567 0.527 0.458 | 188 195 237 257 317 329 460 478 651 672 876 902 1414 | - - - - 296 308 431 449 616 637 836 862 1357 |
| 12×0.75 12×0.75 12×1.0 12×1.0 12×1.5 12×1.5 12×2.5 12×2.5 | 1 2 1 2 1 2 1 2 | 0.6／- 0.6／- 0.6／- 0.6／- 0.7／0.7 0.7／0.7 0.8／0.7 0.8／0.7 | 1.5 1.5 1.5 1.5 1.5 1.5 1.5 1.5 | 11.5／- 11.5／- 12.0／- 12.5／- 14.0／14.0 14.0／14.0 16.0／15.2 16.5／15.7 | 13.5／- 14.5／- 14.5／- 15.5／- 16.5／16.5 17.5／17.5 19.0／18.2 20.5／19.7 | 0.012 0.014 0.011 0.013 0.011 0.010 0.010 0.009 | - - - - 0.948 0.863 0.785 0.707 | 229 239 268 291 362 375 530 540 | - - - - 348 360 500 518 |

Type: KVV（KYJV）  Rated Voltage: 450／750V（600／1000V）                     Table 5 (3) continued

| No. of Cores× Nominal Cross-section mm2 | Kind of Conductor | Nominal Thickness of Insulation mm | Nominal Thickness of Sheath mm | Average Outer Diameter mm |  | Min. Insulation Resistance at 70℃／90℃（PVC／XLPE） MΩ·km |  | Approx. Weight kg／km |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Lower Limit | Uppe limit |  |  |  |  |
|  |  |  |  |  |  | KVV | KYJV | KVV | KYJV |
| 12×4 12×4 12×6 12×6 | 1 2 1 2 | 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 | 1.7 1.7 1.7 1.7 | 18.5／17.7 19.0／18.2 20.5／19.7 21.0／20.2 | 21.5／20.7 23.0／22.2 23.5／22.7 26.0／25.2 | 0.0085 0.0077 0.0070 0.0065 | 0.664 0.601 0.567 0.527 | 753 778 1020 1050 | 723 747 979 1008 |
| 14×0.75 14×0.75 14×1.0 14×1.0 14×1.5 14×1.5 14×2.5 14×2.5 14×4 14×4 14×6 14×6 | 1 2 1 2 1 2 1 2 1 2 1 2 | 0.6／- 0.6／- 0.6／- 0.6／- 0.7／0.7 0.7／0.7 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 0.8／0.7 | 1.5 1.5 1.5 1.5 1.5 1.5 1.5 1.5 1.7 1.7 1.7 1.7 | 12.0／- 12.0／- 12.5／- 13.0／- 14.5／14.5 15.0／15.0 17.0／16.1 17.5／16.6 19.5／18.6 20.0／19.1 21.5／20.6 22.5／21.6 | 14.5／- 15.0／- 15.0／- 16.0／- 17.0／17.0 18.5／18.5 19.5／18.6 21.5／20.6 22.5／21.6 24.5／23.6 24.5／23.6 27.0／26.1 | 0.012 0.014 0.011 0.013 0.011 0.010 0.010 0.009 0.0085 0.0077 0.0070 0.0065 | - - - - 0.949 0.863 0.785 0.707 0.664 0.601 0.567 0.527 | 257 267 302 328 409 424 603 625 860 887 1169 1202 | - - - - 380 395 562 584 811 838 1122 1142 |
| 16×0.75 16×0.75 16×1.0 16×1.0 16×1.5 16×1.5 16×2.5 16×2.5 | 1 2 1 2 1 2 1 2 | 0.6／- 0.6／- 0.6／- 0.6／- 0.7／0.7 0.7／0.7 0.8／0.7 0.8／0.7 | 1.5 1.5 1.5 1.5 1.5 1.5 1.7 1.7 | 12.5／- 13.0／- 13.0／- 13.5／- 15.0／15.0 15.5／15.5 18.0／17.1 19.0／18.1 | 15.0／- 16.0／- 15.5／- 17.0／- 18.0／18.0 19.5／19.5 21.0／20.1 23.0／22.1 | 0.012 0.014 0.011 0.013 0.011 0.010 0.010 0.009 | - - - - 0.948 0.863 0.783 0.707 | 284 296 335 365 456 472 694 720 | - - - - 438 453 666 691 |
| 19×0.75 19×0.75 19×1.0 19×1.0 19×1.5 19×1.5 19×2.5 19×2.5 | 1 2 1 2 1 2 1 2 | 0.6／- 0.6／- 0.6／- 0.6／- 0.7／0.7 0.7／0.7 0.8／0.7 0.8／0.7 | 1.5 1.5 1.5 1.5 1.5 1.5 1.7 1.7 | 13.0／- 13.5／- 14.0／- 14.5／- 16.0／16.0 16.5／16.5 19.0／18.0 20.0／19.0 | 15.5／- 16.5／- 16.5／- 17.5／- 19.0／19.0 20.5／20.5 22.0／21.0 24.0／23.0 | 0.012 0.014 0.011 0.013 0.011 0.010 0.010 0.009 | - - - - 0.949 0.863 0.785 0.707 | 323 336 383 418 525 843 801 835 | - - - - 486 524 745 779 |
| 24×0.75 | 1 | 0.6／- | 1.5 | 15.0／- | 18.0／- | 0.012 | - | 398 | - |

Type: KVV（KYJV）  Rated Voltage: 450／750V（600／1000V）                     Table 5 (4) continued

| No. of Cores× Nominal Cross-section mm2 | Kind of Conductor | Nominal Thickness of Insulation mm | Nominal Thickness of Sheath mm | Average Outer Diameter mm |  | Min. Insulation Resistance at 70℃／90℃（PVC／XLPE） MΩ·km |  | Approx. Weight kg／km |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Lower Limit | Uppe limit |  |  |  |  |
|  |  |  |  |  |  | KVV | KYJV | KVV | KYJV |
| 24×0.75 24×1.0 24×1.0 24×1.5 24×1.5 24×2.5 24×2.5 | 2 1 2 1 2 1 2 | 0.6／- 0.6／- 0.6／- 0.7／0.7 0.7／0.7 0.8／0.7 0.8／0.7 | 1.5 1.5 1.5 1.7 1.7 1.7 1.7 | 15.5／- 16.0／- 16.5／- 19.0／19.0 20.0／20.0 22.5／21.4 23.0／21.9 | 19.0／- 19.0／- 20.5／- 22.0／22.0 24.0／24.0 25.5／24.4 28.0／26.9 | 0.014 0.011 0.013 0.011 0.010 0.010 0.009 | - - - 0.949 0.803 0.785 0.707 | 414 462 480 669 692 996 1080 | - - - 636 657 946 1026 |
| 27×0.75 27×0.75 27×1.0 27×1.0 27×1.5 27×1.5 27×2.5 27×2.5 | 1 2 1 2 1 2 1 2 | 0.6／- 0.6／- 0.6／- 0.6／- 0.7／0.7 0.7／0.7 0.8／0.7 0.8／0.7 | 1.5 1.5 1.5 1.5 1.7 1.7 1.7 1.7 | 15.5／- 16.0／- 16.5／- 17.0／- 19.5／19.5 20.0／20.0 23.0／21.8 23.5／22.3 | 18.0／- 19.5／- 19.0／- 20.5／- 22.5／22.5 24.5／24.5 26.0／24.8 28.5／27.3 | 0.012 0.014 0.011 0.013 0.011 0.010 0.010 0.009 | - - - - 0.949 0.863 0.785 0.707 | 435 452 518 566 734 759 1099 1139 | - - - - 697 721 1044 1182 |
| 30×0.75 30×0.75 30×1.0 30×1.0 30×1.5 30×1.5 30×2.5 30×2.5 | 1 2 1 2 1 2 1 2 | 0.6／- 0.6／- 0.6／- 0.6／- 0.7／0.7 0.7／0.7 0.8／0.7 0.8／0.7 | 1.5 1.5 1.7 1.7 1.7 1.7 1.7 1.7 | 16.0／- 16.5／- 17.5／- 18.0／- 20.0／20.0 21.0／21.0 24.0／22.7 24.5／23.2 | 19.0／- 20.0／- 20.5／- 22.0／- 23.0／23.0 25.0／25.0 27.0／25.7 29.5／28.2 | 0.012 0.014 0.011 0.013 0.011 0.010 0.010 0.009 | - - - - 0.949 0.863 0.785 0.707 | 473 492 582 635 802 830 1206 1249 | - - - - 762 789 1146 1187 |
| 37×0.75 37×0.75 37×1.0 37×1.0 37×1.5 37×1.5 37×2.5 37×2.5 | 1 2 1 2 1 2 1 2 | 0.6／- 0.6／- 0.6／- 0.6／- 0.7／0.7 0.7／0.7 0.8／0.7 0.8／0.7 | 1.7 1.7 1.7 1.7 1.7 1.7 1.7 1.7 | 17.5／- 18.0／- 18.5／- 19.5／- 21.5／21.5 22.5／22.5 25.5／24.1 26.5／25.1 | 20.5／- 22.0／- 21.5／- 23.5／- 25.0／25.0 27.0／27.0 29.0／27.6 31.5／30.1 | 0.012 0.014 0.011 0.013 0.011 0.010 0.010 0.009 | - - - - 0.949 0.863 0.785 0.707 | 579 602 693 757 961 993 1453 1504 | - - - - 884 916 1344 1395 |

Type: KVVP（KYJVP）  Rated Voltage: 450／750V（600／1000V）               Table: 6

| No. of Cores× Nominal Cross- section mm2 | Kind of Conductor | Nominal Thickness of Insulation mm | Diameter of Screened Single Wire mm | Nominal Thickness of Sheath mm | Average Outer Diameter mm |  | Min. Insulation Resistance at 70℃／90℃（PVC／XLPE） MΩ·km |  | Approx. Weight kg／km |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Lower Limit | Upper Limit |  |  |  |  |
|  |  |  |  |  |  |  | KVVP | KYJVP | KVV | KYJVP |
| 2×0.75 2×1.0 2×1.5 2×2.5 2×4 2×6 2×10 | 2 2 2 2 2 2 2 | 0.6／- 0.6／- 0.7／0.7 0.8／0.7 0.8／0.7 0.8／0.7 1.0／0.7 | 0.15 0.15 0.15 0.15 0.20 0.20 0.20 | 0.15 0.15 0.15 0.15 0.20 0.20 0.20 | 7.8／- 8.2／- 9.2／9.2 10.0／9.6 11.5／11.1 13.0／12.6 15.5／14.3 | 9.8／- 10.5／- 11.5／11.5 12.5／12.1 14.5／14.1 16.0／15.6 19.0／17.8 | 0.014 0.013 0.010 0.009 0.0077 0.0065 0.0065 | - - 0.863 0.707 0.601 0.527 0.458 | 94 107 127 169 242 297 428 | - - 122 162 232 285 411 |
| 3×0.75 3×1.0 3×1.5 3×2.5 3×4 3×6 3×10 | 2 2 2 2 2 2 2 | 0.6/一 0.6/一 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 1.0/0.7 | 0.15 0.15 0.15 0.15 0.20 0.20 0.20 | 1.2 1.2 1.2 1.2 1.5 1.5 1.5 | 8.2/一 8.6/一 9.6/9.6 10.5/10.1 12.5/12.1 13.5/13.1 16.5/15.2 | 10.5/一 10.5/一 12.0/12.0 13.5/13.1 15.5/15.1 17.0/16.6 20.0/18.7 | 0.014 0.013 0.010 0.009 0.0077 0.0065 0.0065 | - - 0.863 0.707 0.607 0.527 0.458 | 111 126 157 209 299 377 555 | - - 151 201 287 362 533 |
| 4×0.75 4×1.0 4×1.5 4×2.5 4×4 4×6 4×10 | 2 2 2 2 2 2 2 | 0.6/一 0.6/一 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 1.0/0.7 | 0.15 0.15 0.15 0.20 0.20 0.20 0.20 | 1.2 1.2 1.2 1.5 1.5 1.5 1.7 | 8.8/一 9.2/一 10.0/10.0 12.5/12.0 13.5/13.0 15.0/14.5 18.0/16.6 | 11.0/一 11.5/一 12.5/12.5 15.0/14.5 16.5/16.0 18.0/17.5 22.0/20.6 | 0.014 0.013 0.010 0.009 0.0077 0.0065 0.0065 | - - 0.863 0.707 0.601 0.527 0.458 | 129 149 184 284 365 467 712 | - - 176 272 351 451 684 |
| 5×0.75 5×1.0 5×1.5 5×2.5 5×4 5×6 5×10 | 2 2 2 2 2 2 2 | 0.6/一 0.6/一 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 1.0/0.7 | 0.15 0.15 0.15 0.20 0.20 0.20 0.20 | 1.2 1.2 1.2 1.5 1.5 1.5 1.7 | 9.4/一 9.8/一 11.0/11.0 13.5/13.0 14.5/14.0 16.0/15.5 19.5/17.9 | 11.5/一 12.0/一 13.5/13.5 16.5/16.0 18.0/17.5 19.5/18.0 24.0/22.4 | 0.014 0.013 0.010 0.009 0.0077 0.0065 0.0065 | - - 0.863 0.707 0.601 0.527 0.458 | 148 173 215 332 431 455 854 | - - 205 317 414 435 820 |
| 7×0.75 7×1.0 7×1.5 | 2 2 2 | 0.6/一 0.6/一 0.7/0.7 | 0.15 0.15 0.15 | 1，2 1.2 1.5 | 10.0/一 10.5/一 12.5/12.5 | 12.5/一 13.0/一 15.0/15.0 | 0.014 0.013 0.010 | - - 0.863 | 179 212 283 | - - 269 |

Type: KVVP（KYJVP）  Rated Voltage: 450／750V（600／1000V）                   Table 6 continued

| No. of Cores× Nominal Cross- section mm2 | Kind of Conductor | Nominal Thickness of Insulation mm | Diameter of Screened Single Wire mm | Nominal Thickness of Sheath mm | Average Outer Diameter mm |  | Min. Insulation Resistance at 70℃／90℃（PVC／XLPE） MΩ·km |  | Approx. Weight kg／km |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Lower Limit | Upper Limit |  |  |  |  |
|  |  |  |  |  |  |  | KVVP | KYJVP | KVV | KYJVP |
| 7×2.5 7×4 7×6 7×10 | 2 2 2 2 | 0.8/0.7 0.8/0.7 0.8/0.7 1.0/0.7 | 0.20 0.20 0.20 0.20 | 1.5 1.5 1.5 1.7 | 14.5/13.9 15.5/14.9 17.5/16.9 21.5/19.7 | 17.5/16.9 19.0/18.4 21.0/20.4 26.0/24.2 | 0.009 0.0077 0.0065 0.0065 | 0.707 0.601 0.527 0.458 | 414 549 716 1114 | 397 527 687 1069 |
| 8×0.75 8×1.0 8×1.5 8×2.5 8×4 8×6 8×10 | 2 2 2 2 2 2 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 1.0/0.7 | 0.15 0.15 0.20 0.20 0.20 0.20 0.25 | 1.2 1.5 1.5 1.5 1.7 1.7 1.7 | 11.0/- 12.0/- 14.0/14.0 16.0/15.3 18.0/17.3 19.5/18.8 24.0/22.0 | 13.5/- 15.0/- 17.0/17.0 19.0/18.3 21.5/20.8 24.0/23.3 29.0/27.0 | 0.014 0.013 0.010 0.009 0.0077 0.0065 0.0065 | - - 0.863 0.707 0.601 0.527 0.458 | 198 256 331 367 639 823 1287 | - - 318 352 613 790 1236 |
| 10×0.75 10×1.0 10×1.5 10×2.5 10×4 10×6 10×10 | 2 2 2 2 2 2 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 1.0/0.7 | 0.20 0.20 0.20 0.20 0.20 0.25 0.25 | 1.5 1.5 1.5 1.5 1.7 1.7 1.7 | 13.0/- 13.5/- 15.5/15.5 17.5/16.7 20.0/19.2 22.5/21.7 27.0/24.6 | 16.0/— 16.5/- 18.5/18.5 21.5/20.7 24.0/23.2 27.0/26.2 32.5/30.1 | 0.014 0.013 0.010 0.009 0.0077 0.0065 0.0065 | - - 0.863 0.707 0.601 0.527 0.458 | 271 320 402 565 771 1041 1588 | - - 386 542 740 999 1524 |
| 12×0.75 12×1.0 12×1.5 12×2.5 12×4 12×6 | 2 2 2 2 2 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 | 0.20 0.20 0.20 0.20 0.20 0.25 | 1.5 1.5 1.5 1.7 1.7 1.7 | 13.0/- 14.0/- 16.0/16.0 18.5/17.7 20.5/19.7 23.O/22.2 | 16.0/- 17.0/- 19.0/19.0 22.5/21.7 25.0/24.2 27.5/26.7 | 0.014 0.013 0.010 0.0CG 0.0077 0.0065 | - - 0.863 0.707 0.601 0.527 | 300 356 450 656 879 1193 | - - 432 630 845 1145 |
| 14×0.75 14×1.0 14×1.5 14×2.5 14×4 14×6 | 2 2 2 2 2 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 | 0.20 0.20 0.20 0.20 0.20 0.25 | 1.5 1.5 1.5 1.7 1.7 1.7 | 14.0/- 14.5/- 16.5/16.5 19.5/18.6 21.5/20.6 24.0/23.1 | 17.O/- 17.5/- 20.0/20.0 23.5/22.6 26.0/25.1 29.0/28.1 | 0.014 0.013 0.010 0.009 0.0077 0.0065 | - - 0.863 0.707 0.601 0.527 | 331 397 503 738 994 1353 | - - 483 708 954 1299 |
| 16×0.75 | 2 | 0.6/- | 0.20 | 1.5 | 14.5/- | 17.5/- | 0.014 | - | 363 | - |

Type: KVVP（KYJVP）  Rated Voltage: 450／750V（600／1000V）                   Table 6 continued

| KYJVP KYJVP KYJVP | KVV KVV KVV | KYJVP KYJVP KYJVP | KYJVP KYJVP KYJVP | KVV KVV KVV | KYJVP |  | KYJVP KVV |  | KVV KYJVP |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | KYJVP KYJVP | KYJVP KYJVP |  |  |  |
|  |  |  |  |  |  |  | KVV | KYJVP | KYJVP | KVV |
| 16×1.0 16×1.5 16×2.5 | 2 2 2 | 0.6/- 0.7/0.7 0.8/0.7 | 0.20 0.20 0.20 | 1.5 1.5 1.7 | 15.0/- 17.5/17.5 20.5/19.6 | 18.5/- 21.0/21.0 24.0/23.1 | 0.013 0.010 0.009 | - 0.863 0.707 | 437 556 810 | - 534 778 |
| 19×0.75 19×1.0 19×1.5 19×2.5 | 2 2 2 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 0.20 0.20 0.20 0.20 | 1.5 1.5 1.7 1.7 | 15.0/- 16.0/- 18.5/18.5 21.5/20.5 | 18.0/- 19.0/- 22.5/22.5 25.5/24.5 | 0.014 0.013 0.010 0.009 | - - 0.863 0.707 | 406 494 621 942 | - - 596 904 |
| 24×0.75 24×1.0 24×1.5 24×2.5 | 2 2 2 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 0.20 0.20 0.20 0.25 | 1.5 1.7 1.7 1.7 | 17.0/- 18.5/- 21.5/21.5 25.0/23.9 | 20.5/- 22.0/— 25.5/25.5 29.5/28.4 | 0.014 0.013 0.010 0.009 | - - 0.863 0.707 | 498 622 797 1191 | - - 765 1143 |
| 27×0.75 27×1.0 27×1.5 27×2.5 | 2 2 2 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 0.20 0.20 0.20 0.25 | 1.5 1.7 1.7 1.7 | 17.5/- 19.0/- 21.5/21.5 25.5/24.3 | 21.0/- 22.5/— 26.0/26.0 30.5/29.3 | 0.014 0.013 0.010 0.009 | - - 0.863 0.707 | 537 674 866 1301 | - - 831 1249 |
| 30×0.75 30×1.0 30×1.5 30×2.5 | 2 2 2 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 0.20 0.20 0.25 0.25 | 1.7 1.7 1.7 1.7 | 18.5/- 19.5/- 22.5/22.5 26.5/25.2 | 22.0/- 23.5/— 27.0/27.0 31.5/30.2 | 0.014 0.013 0.010 0.009 | - - 0.863 0.707 | 597 730 969 1301 | - - 930 1249 |
| 37×0.75 37×1.0 37×1.5 37×2.5 | 2 2 2 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 0.20 0.20 0.25 0.25 | 1.7 1.7 1.7 2.0 | 19.5/- 21.0/- 24.5/24.5 29.0/27.6 | 23.5/- 25.0/- 29.0/29.0 34.0/32.6 | 0.014 0.013 0.010 0.O09 | - - 0.863 0.707 | 724 843 1185 1417 | - - 1138 1360 |

Type: KVVP2（KYJVP2）  Rated Voltage: 450／750V（600／1000V）                       Table 7

| No. of Cores× Nominal Cross-section mm2 | Kind of Conductor | Nomiinal Thickness of Insulation mm | Nominal Diameter of Screened Copper Tape mm | Nominal Thickness of Sheath mm | Average Overall Diameter mm |  | Min. Insulation Resistance at 70℃／90℃（PVC／XLPE） MΩ·km |  | Approx. Weight kg／km |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Lower Limit | Upper Limit |  |  |  |  |
|  |  |  |  |  |  |  | KVVP2 | KYJVP2 | KVVP2 | KYJVP2 |
| 4×0.75 4×1.0 4×1.5 4×2.5 4×4 4×6 4×10 | 1 1 1 1 1 1 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 1.0/0.7 | 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 | 1.2 1.2 1.2 1.5 1.5 1.5 1.7 | 8.0/- 8.4/- 9.4/9.4 11.0/10.5 12.5/12.0 13.5/13.0 17.5/16.1 | 10.0/- 10.5/- 11.5/11.5 14.0/13.5 15.0/14.5 16.0/15.5 21.5/20.1 | 0.012 0.011 0.011 0.010 0.0085 0.0070 0.0065 | - - 0.948 0.785 0.664 0.567 0.458 | 120 135 172 252 329 427 681 | - - 165 242 315 411 653 |
| 5×0.75 5×1.0 5×1.5 5×2.5 5×4 5×6 5×10 | 1 1 1 1 1 1 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 1.0/0.7 | 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 | 1.2 1.2 1.5 1.5 1.5 1.5 1.７ | 8.6/- 9.0/- 10.0/10.0 12.0/11.5 13.5/13.0 14.5/14.0 19.0/17.4 | 11.0/- 11.0/- 12.5/12.5 15.0/14.5 16.0/15.5 17.5/17.0 23.5/21.9 | 0.012 0.011 0.011 0.010 0.0085 0.0070 0.0065 | - - 0.949 0.785 0.664 0.567 0.458 | 134 156 216 297 391 510 820 | - - 207 285 375 490 787 |
| 7×0.75 7×1.0 7×1.5 7×2.5 7×4 7×6 7×10 | 1 1 1 1 1 1 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 1.0/0.7 | 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 | 1.2 1.2 1.5 1.5 1.5 1.5 1.7 | 9.2/- 9.6/- 11.5/11.5 13.0/12.4 14.5/13.9 16.0/15.4 20.5/18.7 | 11.5/- 12.0/- 14.0/14.0 16.0/15.4 17.5/16.9 19.0/18.4 25.0/22.2 | 0.012 0.011 0.011 0.010 0.0085 0.0070 0.0065 | - - 0.949 0.785 0.664 0.567 0.458 | 167 193 267 382 502 664 1053 | - - 256 367 482 637 1011 |
| 8×0.75 8×1.0 8×1.5 8×2.5 8×4 8×6 8×10 | 1 1 1 1 1 1 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.７ 1.0/0.7 | 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 | 1.5 1.5 1.5 1.5 1.7 1.7 1.7 | 10.0/- 11.0/- 12.5/12.5 14.5/13.8 16.0/15.3 18.0/17.3 23.0/21.0 | 12.5/- 13.5/- 15.5/15.5 17.5/16.8 19.0/18.3 21.0/20.3 28.0/26.0 | 0.012 0.011 0.011 0.010 0.0085 0.0070 0.0065 | - - 0.949 0.785 0.664 0.567 0.458 | 199 228 397 419 627 762 1217 | - - 381 402 602 732 1168 |
| 10×0.75 10×1.0 10×1.5 10×2.5 10×4 10×6 10×10 | 1 1 1 1 1 1 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 1.0/0.7 | 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 | 1.5 1.5 1.5 1.7 1.7 1.7 1.7 | 11.5/- 12.5/- 14.0/14.0 16.5/15.7 18.5/17.7 20.5/19.7 26.0/23.6 | 14.5/- 15.0/- 17.0/17.0 19.5/18.7 21.5/20.7 23.5/22.7 31.5/29.1 | 0.012 0.011 0.011 0.010 0.0085 0.0070 0.0065 | - - 0.949 0.785 0.664 0.567 0.458 | 240 276 362 528 710 943 1504 | - - 348 507 682 905 1444 |
| 12×0.75 | 1 | 0.6/- | 0.05-0.15 | 1.5 | 12.0/- | 14.5/- | 0.012 | - | 267 |  |

Type: KVVP2（KYJVP2）  Rated Voltage: 450／750V（600／1000V）     Table 7 continued

| No. of Cores× Nominal Cross-section mm2 | Kind of Conductor | Nominal Thickness of Insulation mm | Nominal Thickness of Screened Copper Tape mm | Nominal Thickness of Sheath mm | Average Overall Diameter mm |  | Min. Insulation Resistance at 70℃／90℃（PVC／XLPE） MΩ·km |  | Approx. Weight kg／km |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Lower Limet | Upper Limit |  |  |  |  |
|  |  |  |  |  |  |  | KVVP2 | KYJVP2 | KVVP2 | KYJVP2 |
| 12×1.0 12×1.5 12×2.5 12×4 12× 6 | 1 1 1 1 1 | 0.6/- 0.7/0.7 0.8/0.7 0.8/0.? 0.8/0.7 | 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 | 1.5 1.5 1.7 1.7 1.7 | 12.5/- 14.5/14.5 17.0/16.2 19.0/18.2 21.0/20.2 | 15.5/- 17.5/17.5 20.5/19.7 22.5/21.7 24.5/22.7 | 0.011 0.011 0.010 0.0085 0.0070 | - 0.949 0.785 0.664 0.567 | 308 408 600 815 1090 | - 392 576 782 1064 |
| 14×0.75 14×1.0 14×1.5 14×2.5 14×4 14×6 | 1 1 1 1 1 1 | 0.6/- 0.6/- 0.7/0.7 0.8/0.8 0.8/0.8 0.8/0.8 | 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 | 1.5 1.5 1.5 1.7 1.7 1.7 | 12.5/- 13.5/- 15.0/15.0 18.0/17.1 20.0/19.1 22.0/21.1 | 15.5/- 16.0/- 18.0/18.0 21.0/20.1 23.5/22.6 25.5/24.6 | 0.012 0.011 0.011 0.010 0.0085 0.0070 | - - 0.949 0.785 0.664 0.567 | 296 343 457 677 975 1243 | - - 439 650 936 1193 |
| 16×0.75 16×1.0 16×1.5 16×2.5 | 1 1 1 1 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 | 1.5 1.5 1.5 1.7 | 13.0/- 14.0/- 16.0/16.0 19.0/18.1 | 16.0/- 16.5/- 19.0/19.0 22.0/21.1 | 0.012 0.011 0.011 0.010 | - - 0.949 0.785 | 325 379 508 755 | - - 488 725 |
| 19×0.75 19×1.0 19×1.5 19×2.5 | 1 1 1 1 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 | 1.5 1.5 1.7 1.7 | 14.0/- 14.5/- 16.5/16.5 20.0/19.0 | 16.5/- 17.5/- 20.0/20.0 23.0/22.0 | 0.012 0.011 0.011 0.010 | - - 0.949 0.785 | 367 430 595 866 | - - 571 831 |
| 24×0.75 24×1.0 24×1.5 24×2.5 | 1 1 1 1 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 | 1.5 1.7 1.7 1.7 | 16.0/- 17.0/- 20.0/20.0 23.0/21.9 | 19.0/- 20.5/- 23.0/23.0 26.5/25.4 | 0.012 0.011 0.011 0.0{0 | - - 0.949 0.785 | 449 532 735 1073 | - - 706 1030 |
| 27×0.75 27×1.0 27×1.5 27×2.5 | 1 1 1 1 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 | 1.7 1.7 1.7 1.7 | 16.0/- 17.5/- 20.0/20.0 23.5/22.3 | 19.0/- 20.5/- 23.5/23.5 27.0/25.8 | 0.012 0.011 0.011 0.010 | - - 0.949 0.785 | 502 590 800 1178 | - - 768 1131 |
| 30×0.75 30×1.0 30×1.5 30×2.5 | 1 1 1 1 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 | 1.7 1.7 1.7 1.7 | 17.0/- 18.0/- 21.0/21.0 24.5/23.2 | 20.0/- 21.5/- 24.0/24.0 28.0/26.7 | 0.012 0.011 0.011 0.010 | - - 0.949 0.785 | 543 640 870 1287 | - - 835 1236 |
| 37×0.75 37×1.0 37×1.5 37×2.5 | 1 1 1 1 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 0.05-0.15 0.05-0.15 0.05-0.15 0.05-0.15 | 1.7 1.7 1.7 2.0 | 18.5/- 19.5/- 22.5/22.5 26.5/25.1 | 21.5/- 22.5/- 26.0/26.0 30.0/28.6 | 0.012 0.011 0.011 0.010 | - - 0.949 0.785 | 638 756 1035 1578 | - - 994 1515 |

Type: KVV22（KYJV22）  Rated Voltage: 450／750V（600／1000V）              Table 8

| No. of Cores×Nominal Cross-section mm2 | Knid of Conductor | Nominal Thickness of Insulation mm | Layers of Steel Tape×Thickness mm | Nominal Thickness of Sheath mm | Average Overall Diameter mm |  | Min. Insulation Resistance at 70℃／90℃（PVC／XLPE） MΩ·km |  | Approx. Weight kg／km |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Lower Limit | Upper Limit |  |  |  |  |
|  |  |  |  |  |  |  | KVVP2 | KYJVP2 | KVVP2 | KYJVP2 |
| 4×2.5 4×4 4×6 4×10 | 1 1 1 2 | 0.8/0.7 0.8/0.7 0.8/0.7 1.0/0.7 | 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) | 1.5 1.5 1.5 1.7 | 13.0/12.5 14.0/13.5 15.5/15.0 19.0/17.6 | 17.0/16.5 18.5/18.0 19.0/18.5 25.0/23.6 | 0.010 0.0085 0.0070 0.0065 | 0.785 0.664 0.567 0.458 | 439 526 640 948 | 427 512 614 919 |
| 5×2.5 5×4 5×6 5×10 | 1 1 1 2 | 0.8/0.7 0.8/0.7 0.8/0.7 1.0/0.7 | 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) | 1.5 1.5 1.7 1.7 | 14.0/13.5 15.0/14.5 17.0/16.5 20.0/18.9 | 18.0/17.5 19.5/19.0 21.5/21.0 26.5/24.9 | 0.010 0.0085 0.0070 0.0065 | 0.785 0.664 0.567 0.458 | 497 603 757 1078 | 482 579 727 1035 |
| 7×0.75 7×1.0 7×1.5 7×2.5 7×4 7×6 7×10 | 1 1 1 1 1 1 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 1.0/0.7 | 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) | 1.5 1.5 1.5 1.5 1.5 1.7 1.7 | 11.5/- 12.0/- 13.5/13.5 15.0/14.4 16.5/15.9 18.0/17.4 22.5/20.7 | 15.5/- 16.0/- 17.5/17.5 19.0/18.4 20.5/19.9 22.5/21.9 28.5/26.7 | 0.012 0.011 0.011 0.010 0.0085 0.0070 0.0065 | - - 0.949 0.785 0.664 0.567 0.458 | 345 376 443 590 729 930 1394 | - - 425 566 700 893 1338 |
| 8×0.75 8×1.0 8×1.5 8×2.5 8×4 8×6 8×10 | 1 1 1 1 1 1 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 1.0/0.7 | 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) | 1.5 1.5 1.5 1.5 1.7 1.7 1.7 | 12.5/- 13.0/- 14.5/14.5 16.5/15.8 18.5/17.8 20.0/19.3 25.0/23.0 | 16.5/- 17.0/- 18.5/18.5 21.0/20.3 23.0/22.3 24.5/23.8 31.5/29.5 | 0.012 0.011 0.011 0.0{0 0.0085 0.0070 0.0065 | - - 0.949 0.785 0.664 0.567 0.458 | 443 482 564 753 940 1164 1718 | - - 541 723 902 1117 1649 |
| 10×0.75 10×1.0 10×1.5 10×2.5 10×4 10×6 10×10 | 1 1 1 1 1 1 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 1.0/0.7 | 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) | 1.5 1.5 1.5 1.7 1.7 1.7 2.0 | 13.5/- 14.5/- 16.0/16.0 18.5/17.7 20.5/19.7 22.5/21.7 28.5/26.1 | 18.0/- 18.5/- 20.5/20.5 23.0/22.2 25.0/24.2 27.0/26.2 35.0/31.6 | 0.012 0.011 0.011 0.010 0.0085 0.0070 0.0065 | - - 0.949 0.785 0.664 0.567 0.458 | 518 566 667 938 1130 1403 2150 | - - 640 900 1085 1347 2064 |
| 12×0.75 12×1.0 12×1.5 12×2.5 | 1 1 1 2 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) | 1.5 1.5 1.5 1.7 | 14.0/- 14.5/- 16.5/16.5 19.0/18.2 | 18.0/- 19.0/- 20.5/20.5 23.5/22.7 | 0.012 0.011 0.011 0.010 | - - 0.949 0.785 | 553 608 723 1004 | - - 694 964 |

Type: KVV22（KYJV22）  Rated Voltage: 450／750V（600／1000V）        Table 8 continued

| No. of Cores×Nominal Cross-section mm2 | Kind of Conductor | Nominal Thickness of Insulation mm | Layers of Steel Tape×Thickness mm | Nominal Thickness of Sheathmm | Average Overall Diameter mm |  | Min. Insulation Resistance at 70℃／90℃（PVC／XLPE） MΩ·km |  | Approx. Weight kg／km |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Lower Limit | Upper Limit |  |  |  |  |
|  |  |  |  |  |  |  | KVVP2 | KYJVP2 | KVVP2 | KYJVP2 |
| 12×4 12×6 | 1 1 | 0.8/0.7 0.8/0.7 | 2×0.2(0.3) 2×0.2(0.3) | 1.7 1.7 | 21.0/20.2 23.0/22.2 | 25.5/24.7 28.0/27.2 | 0.0085 0.0070 | 0.664 0.567 | 1248 1596 | 1198 1506 |
| 14×0.75 14×1.0 14×1.5 14×2.5 14× 4 14×6 | 1 1 1 1 1 1 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 | 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) | 1.5 1.5 1.7 1.7 1.7 1.7 | 14.5/- 15.0/- 17.5/17.5 20.0/19.1 22.0/21.1 24.0/23.1 | 18.5/- 19.5/- 22.0/22.0 24.5/23.6 26.5/25.6 29.0/28.1 | 0.012 0.011 0.011 0.010 0.0085 0.0070 | - - 0.949 0.785 0.664 0.567 | 595 656 805 1104 1199 1747 | 571 630 773 1060 1151 1677 |
| 16 ×0.75 16×1.0 16×1.5 16×2.5 | 1 1 1 1 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) | 1.5 1.5 1.7 1.7 | 15.0/- 16.0/- 18.0/18.0 21.0/20.1 | 19.5/- 20.0/- 22.5/22.5 25.5/24.6 | 0.012 0.011 0.011 0.010 | - - 0.949 0.785 | 640 708 873 1203 | - - 838 1155 |
| 19×0.75 19×1.0 19×1.5 19×2.5 | 1 1 1 1 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) | 1.5 1.7 1.7 1.7 | 15.5/- 17.0/- 19.0/19.0 22.0/21.0 | 20.0/- 21.5/- 23.5/23.5 26.5/25.5 | 0.012 0.011 0.011 0.010 | - - 0.949 0.785 | 697 788 949 1340 | - - 911 1286 |
| 24×0.75 24×1.0 24×1.5 24×2.5 | 1 1 1 1 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) | 1.7 1.7 1.7 1.7 | 18.0/- 19.0/- 21.5/21.5 25.0/23.9 | 22.5/- 23.5/- 26.5/26.5 30.0/28.9 | 0.012 0.011 0.011 0.010 | - - 0.949 0.785 | 1021 1139 1159 1625 | - - 1113 1560 |
| 27×0.75 27×1.0 27×1.5 27×2.5 | 1 1 1 1 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) | 1.7 1.7 1.7 1.7 | 18.5/- 19.5/- 22.0/22.0 25.5/24.3 | 23.0/- 24.0/- 27.0/27.0 30.5/29.3 | 0.012 0.011 0.011 0.010 | - - 0.949 0.785 | 894 1001 1237 1745 | - - 1188 1675 |
| 30×0.75 30×1.0 30×1.5 30×2.5 | 1 1 1 1 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) | 1.7 1.7 1.? 1.7 | 19.0/- 20.0/- 23.0/23.0 26.5/25.2 | 23.5/- 24.5/- 27.5/27.5 31.5/30.2 | 0.012 0.011 0.011 0.010 | - - 0.949 0.785 | 949 1065 1324 1873 | - - 1271 1798 |
| 37×0.75 37×1.0 37×1.5 37×2.5 | 1 1 1 1 | 0.6/- 0.6/- 0.7/0.7 0.8/0.7 | 2×0.2(0.3) 2×0.2(0.3) 2×0.2(0.3) 2×0.5 | 1.7 1.7 1.7 2.0 | 20.5/- 21.5/- 24.5/24.5 30.0/28.6 | 25.0/- 26.0/- 29.5/29.5 35.0/33.6 | 0.012 0.011 0.011 0.010 | - - 0.949 0.785 | 1075 1215 1525 2224 | - - 1464 2135 |

Type: KVV32（KYJV32）  Rated Voltage: 450／750V（600／1000V）            Table 9

| No. of Cores×Nominal Cross-section mm2 | Kind of Conductor | Nominal Thickness of Insulation mm | Diameter of thin Steel Wire mm | Nominal Thickness of Sheath mm | Average Overall Diameter mm |  | Min. Insultion Resistance at 70℃／90℃（PVC／XLPE） MΩ·km |  | Approx. Weight kg／km |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Lower Limit | Upper Limit |  |  |  |  |
|  |  |  |  |  |  |  | KVV32 | KYJV32 | KVV32 | KYJV32 |
| 4×4 4×6 4×10 | 1 1 2 | 0.8/0.7 0.8/0.7 1.0/0.7 | 0.8-1.6 0.8-1.6 1.6-2.0 | 1.5 1.5 1.7 | 15.0/14.5 16.0/15.5 21.5/20.1 | 20.5/20.0 21.5/21.0 28.0/26.6 | 0.0085 0.0070 0.0065 | 0.664 0.567 0.458 | 731 878 1396 | 717 860 1368 |
| 5×4 5×6 5×10 | 1 1 2 | 0.8/0.7 0.8/0.7 1.0/0.7 | 0.8-1.6 0.8-1.6 1.6-2.0 | 1.5 1.7 1.7 | 16.0/15.5 17.5/17.0 23.0/21.4 | 21.5/21.0 23.5/23.0 29.5/27.9 | 0.0085 0.0070 0.0065 | 0.664 0.567 0.458 | 842 1030 1592 | 825 1009 1560 |
| 7×1.5 7×2.5 7×4 7×6 7×10 | 1 1 1 1 2 | 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 1.0/0.7 | 0.8-1.6 0.8-1.6 0.8-1.6 0.8-1.6 1.6-2.0 | 1.5 1.5 1.7 1.7 1.7 | 14.0/14.0 16.0/15.4 17.5/16.9 19.0/18.4 24.5/22.7 | 19.5/19.5 21.5/20.9 23.0/22.4 24.5/24.1 31.5/29.7 | 0.011 0.010 0.0085 0.0070 0.0065 | 0.949 0.785 0.664 0.567 0.458 | 626 808 1003 1233 1925 | 613 792 983 1208 1887 |
| 8×1.5 8×2.5 8×4 8×6 8×10 | 1 1 1 1 2 | 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 1.0/0.7 | 0.8-1.6 0.8-1.6 1.6-2.0 1.6-2.0 1.6-2.0 | 1.5 1.7 1.7 1.7 1.7 | 15.5/15.5 17.5/16.8 20.5/19.8 22.5/21.9 27.5/25.5 | 21.0/21.0 23.5/22.8 26.0/25.3 27.5/26.9 34.5/32.5 | 0.011 0.010 0.0085 0.0070 0.0065 | 0.949 0.785 0.664 0.567 0.458 | 673 904 1219 1485 2117 | 660 886 1195 1455 2075 |
| 10×1.5 10×2.5 10×4 10×6 10×10 | 1 1 1 1 2 | 0.7/0.7 0.8/0.? 0.8/0.7 0.8/0.7 1.0/0.7 | 0.8-1.6 1.6-2.0 1.6-2.0 1.6-2.0 1.6-2.0 | 1.7 1.7 1.7 1.7 2.0 | 17.0/17.0 21.0/20.2 22.5/21.7 24.5/23.7 31.0/28.6 | 23.0/23.0 26.0/25.2 28.0/27.2 30.0/29.2 38.5/36.1 | 0.011 0.010 0.0085 0.0070 0.0065 | 0.949 0.785 0.664 0.567 0.458 | 869 1194 1457 1765 2605 | 852 1170 1422 1730 2553 |
| 12×1.5 12×2.5 12×4 12×6 | 1 1 1 1 | 0.7/0.7 0.8/0.7 0.8/0.7 0.8/0.7 | 0.8-1.6 1.6-2.0 1.6-2.0 1.6-2.0 | 1.7 1.7 1.7 1.7 | 17.5/17.5 21.5/20.7 23.5/22.7 25.5/24.7 | 23.5/23.5 26.5/25.7 28.5/27.7 31.0/30.2 | 0.011 0.010 0.0085 0.0070 | 0.949 0.785 0.664 0.567 | 865 1292 1585 1937 | 848 1266 1853 1898 |
| 14×1.5 14×2.5 | 1 1 | 0.7/0.7 0.8/0.7 | 0.8-1.6 1.6-2.0 | 1.7 1.7 | 18.0/18.0 22.5/21.6 | 24.0/24.0 27.5/26.6 | 0.011 0.010 | 0.949 0.785 | 932 1268 | 913 1243 |

Type: KVV32（KYJV32）  Rated Voltage: 450／750V（600／1000V）        Table 9continued

| No. of Cores×Nominal Cross-section mm2 | Kind of Conductor | Nominal Thickness of Insulation mm | Diameter of thin Steel Wire mm | Nominal Thickness of Sheath mm | Average Overall Diameter mm |  | Min. Insulation Resistance at 70℃／90℃（PVC／XLPE） MΩ·km |  | Approx. Weight kg／km |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Lower Limit | Upper Limit |  |  |  |  |
|  |  |  |  |  |  |  | KVV32 | KYJV32 | KVV32 | KYJV32 |
| 14×4 14×6 | 1 1 | 0.8/0.7 0.8/0.7 | 1.6-2.0 1.6-2.0 | 1.7 1.7 | 24.0/23.1 26.5/25.6 | 29.5/28.6 32.0/31.1 | 0.0085 0.0070 | 0.664 0.567 | 1829 2142 | 1792 2099 |
| 16×1.5 16×2.5 | 1 1 | 0.7/0.7 0.8/0.7 | 1.6-2.0 1.6-2.0 | 1.7 1.7 | 20.5/20.5 23.0/23.1 | 25.5/25.5 28.5/27.6 | 0.011 0.010 | 0.949 0.785 | 1152 1528 | 1129 1497 |
| 19×1.5 19×2.5 | 1 1 | 0.7/0.7 0.8/0.7 | 1.6-2.0 1.6-2.0 | 1.7 1.7 | 21.5/21.5 24.0/23.0 | 26.5/26.5 29.5/28.5 | 0.011 0.010 | 0.949 0.785 | 1222 1662 | 1198 1629 |
| 24×1.5 24×2.5 | 1 1 | 0.7/0.7 0.8/0.7 | 1.6-2.0 1.6-2.0 | 1.7 2.0 | 24.0/24.0 28.0/26.9 | 29.5/29.5 33.5/32.4 | 0.011 0.010 | 0.949 0.785 | 1461 2038 | 1432 1997 |
| 27×1.5 27×2.5 | 1 1 | 0.7/0.7 0.8/0.7 | 1.6-2.0 1.6-2.0 | 1.7 2.0 | 24.5/24.5 28.5/27.3 | 30.0/30.0 34.0/32.8 | 0.011 0.010 | 0.949 0.785 | 1554 2170 | 1523 2127 |
| 30×1.5 30×2.5 | 1 1 | 0.7/0.7 0.8/0.7 | 1.6-2.0 1.6-2.0 | 1.7 2.0 | 25.0/25.0 29.5/28.2 | 30.5/30.5 34.5/33.2 | 0.011 0.010 | 0.949 0.785 | 1650 2332 | 1617 2285 |
| 37×1.5 37×2.5 | 1 1 | 0.7/0.7 0.8/0.7 | 1.6-2.0 2.0-2.5 | 2.0 2.2 | 27.5/27.5 32.5/31.1 | 33.0/33.0 38.5/37.1 | 0.011 0.010 | 0.949 0.785 | 1901 2930 | 1683 2871 |

Type: KVVR  Rated Voltage: 450／750V                                 Table 10

| No. of Cores×Nominal Cross- section mm2 | Kind of Conductor | Nominal Thickness of Insulation mm | Nominal Thickness of Sheath mm | Average Overall Diameter mm |  | Min. Insulation Resistance at 70℃／90℃（PVC／XLPE） MΩ·km | Approx. Weight kg／km |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Lower Limt | Upper Limit |  |  |
| 4×0.5 4×0.75 4×1.0 4×1.5 4×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 1.2 1.2 1.2 1.2 1.2 | 7.2 7.6 8.0 9.0 10.5 | 9.0 9.4 10.0 11.5 13.0 | 0.013 0.011 0.010 0.010 0.009 | 86 103 119 151 213 |
| 5×0.5 5×0.75 5×1.0 5×1.5 5×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 1.2 1.2 1.2 1.2 1.5 | 7.8 8.4 8.8 9.8 12.0 | 9.6 10.5 11.0 12.0 14.5 | 0.013 0.011 0.010 0.010 0.009 | 99 109 139 179 272 |
| 7×0.5 7×0.75 7×1.0 7×1.5 7×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 1.2 1.2 1.2 12 1.5 | 8.4 9.0 9.6 10.5 13.0 | 10.5 11.0 11.5 13.0 16.0 | 0.013 0.011 0.010 0.010 0.009 | 121 148 175 228 350 |
| 8×0.5 8×0.75 8×1.0 8×1.5 8×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 1.2 12 1.2 1.5 1.5 | 9.4 10.0 10.5 12.5 15.0 | 11.5 12.0 13.0 15.0 17.5 | 0.013 0.011 0.010 0.010 0.009 | 135 167 196 273 393 |
| 10×0.5 10×0.75 10×1.0 10×1.5 10×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 1.2 1.2 1.5 1.5 1.5 | 10.5 11.0 12.5 14.0 16.5 | 12.5 13.5 15.0 17.0 19.5 | 0.013 0.011 0.010 0.010 0.009 | 163 20O 257 334 483 |
| 12×0.5 12×0.75 12×1.0 12×1.5 12×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 1.2 1.5 1.5 1.5 1.5 | 10.5 12.0 12.5 14.5 17.5 | 13.0 14.5 15.5 17.5 20.5 | 0.013 0.011 0.010 0.010 0.009 | 183 245 290 381 556 |
| 14×0.5 14×0.75 14×1.0 | 5 5 5 | 0.6 0.6 0.6 | 1.2 1.5 1.5 | 11.0 12.5 13.5 | 13.5 15.0 16.0 | 0.013 0.011 0.010 | 206 276 325 |

Type: KVVR  Rated Voltage: 450／750V                        Table 10 continued

| No. of Cores×Nominal Cross- section mm2 | Kind of Conductor | Nominal Thickness of Insulation mm | Nominal Thickness of Sheath mm | Average Overall Diameter mm |  | Min. Insulation Resistance at 70℃／90℃（PVC／XLPE） MΩ·km | Approx. Weight kg／km |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Lower Limit | Upper Limit |  |  |
| 14×1.5 14×2.5 | 5 5 | 0.7 0.8 | 1.5 1.5 | 15.0 18.0 | 18.0 21.0 | 0.010 0.009 | 430 633 |
| 16×0.5 16×0.75 16×1.0 16×1.5 16×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 1.5 1.5 1.5 1.5 1.7 | 12.5 13.5 14.0 16.0 19.5 | 15.0 16.0 17.0 19.0 23.0 | 0.013 0.011 0.010 0.010 0.009 | 244 304 361 480 728 |
| 19×0.5 19×0.75 19×1.0 19×1.5 19×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 1.5 1.5 1.5 1.5 1.7 | 13.0 14.0 15.0 16.5 20.5 | 15.5 16.5 17.5 20.0 24.0 | 0.013 0.011 0.010 0.010 0.009 | 276 346 412 552 840 |
| 24×0.5 24×0.75 24×1.0 24×1.5 24×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 1.5 1.5 1.5 1.7 1.7 | 15.0 16.0 17.0 20.0 24.0 | 18.0 19.0 20.0 23.5 27.5 | 0.013 0.011 0.010 0.010 0.009 | 338 426 556 703 1049 |
| 27×0.5 27×0.75 27×1.0 27×1.5 27×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 1.5 1.5 1.5 1.7 1.7 | 15.0 16.5 17.5 20.5 24.5 | 18.0 19.5 20.5 24.0 28.5 | 0.013 0.011 0.010 0.010 0.009 | 367 465 556 772 1152 |
| 30×0.5 30×0.75 30×1.0 30×1.5 30×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 1.5 1.5 1.7 1.7 1.7 | 16.0 17.0 18.5 21.0 25.5 | 18.5 20.0 21.5 25.0 29.5 | 0.013 0.011 0.010 0.010 0.009 | 399 499 624 843 1663 |
| 37×0.5 37×0.75 37×1.0 37×1.5 37×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 1.5 1.7 1.7 1.7 1.7 | 17.0 19.0 20.0 22.5 27.5 | 20.0 21.5 23.5 27.0 31.5 | 0.013 0.011 0.010 0.010 0.009 | 471 619 741 1009 1521 |

Type: KVVRP  Rated Voltage: 450／750V                                  Table 11

| No. of Cores×Nominal Cross- section mm2 | Kind of Conductor | Nominal Thickness of Insulation mm | Diameter of Screened Single Wire mm | Nominal Thickness of Sheath mm | Average Overall Diameter mm |  | Min. Insulation Resistance at 70℃／90℃（PVC／XLPE） MΩ·km | Approx. Weight kg／km |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Lower Limit | Upper Limit |  |  |
| 4×0.5 4×0.75 4×1.0 4×1.5 4×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 0.15 0.15 0.15 0.15 0.20 | 1.2 1.2 1.2 1.2 1.5 | 8.6 9.0 9.4 10.0 12.5 | 10.5 11.0 11.5 12.5 15.0 | 0.013 0.011 0.010 0.010 0.009 | 113 133 152 187 287 |
| 5×0.5 5×0.75 5×1.0 5×1.5 5×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 0.15 0.15 0.15 0.15 0.20 | 1.2 1.2 1.2 1.2 1.5 | 9.0 9.6 10.0 11.0 13.5 | 11.0 11.5 12.0 13.5 16.0 | 0.013 0.011 0.010 0.010 0.009 | 129 152 176 218 336 |
| 7×0.5 7×0.75 7×1.0 7×1.5 7×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 0.15 0.15 0.15 0.15 0.20 | 1.2 1.2 1.2 1.5 1.5 | 9.8 10.0 10.5 12.5 15.0 | 11.5 12.5 13.0 15.0 17.5 | 0.013 0.011 0.010 0.010 0.009 | 154 183 215 287 419 |
| 8×0.5 8×0.75 8×1.0 8×1.5 8×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 0.15 0.15 0.15 0.20 0.20 | 1.2 1.2 1.5 1.5 1.5 | 10.5 11.0 12.5 14.0 16.5 | 13.0 13.5 15.0 17.0 19.0 | 0.013 0.011 0.010 0.010 0.009 | 168 205 255 336 468 |
| 10×0.5 10×0.75 10×1.0 10×1.5 10×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 0.15 0.20 0.20 0.20 0.20 | 1.5 1.5 1.5 1.5 1.5 | 12.0 13.5 14.0 15.5 18.5 | 14.5 15.5 16.5 18.5 21.0 | 0.013 0.011 0.010 0.010 0.009 | 220 252 325 408 572 |
| 12×0.5 12×0.75 12×1.0 12×1.5 12×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 0.15 0.20 0.20 0.20 0.20 | 1.5 1.5 1.5 1.5 1.7 | 12.5 13.5 14.5 16.0 19.0 | 15.0 16.0 17.0 19.0 22.5 | 0.013 0.011 0.010 0.010 0.009 | 242 308 360 457 665 |
| 14×0.5 14×0.75 14×1.0 | 5 5 5 | 0.6 0.6 0.6 | 0.20 0.20 0.20 | 1.5 1.5 1.5 | 13.5 14.0 15.0 | 16.0 16.5 17.5 | 0.013 0.011 0.010 | 288 341 400 |

Type: KVVRP  Rated Voltage: 450／750V                            Table 11 continued

| No. of Cores×Nominal Cross- section mm2 | Kind of Conductor | Nominal Thickness of Insulation mm | Diameter of Screened Single Wire mm | Nominal Thickness of Sheath mm | Average Overall Diameter mm |  | Min. Insulation Resistance at 70℃／90℃（PVC／XLPE） MΩ·km | Approx. Weight kg／km |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Lower Limit | Upper Limit |  |  |
| 14×1.5 14×2.5 | 5 5 | 0.7 0.8 | 0.20 0.20 | 1.5 1.7 | 16.5 20.0 | 20.0 23.0 | 0.010 0.009 | 510 747 |
| 16×0.5 16×0.75 16×1.0 16×1.5 16×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 0.20 0.20 0.20 0.20 0.20 | 1.5 1.5 1.5 1.5 1.7 | 14.0 15.0 15.5 17.5 21.0 | 16.5 17.5 18.5 20.5 24.5 | 0.013 0.011 0.010 0.010 0.009 | 308 374 440 565 830 |
| 19×0.5 19×0.75 19×1.0 19×1.5 19×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 0.20 0.20 0.20 0.20 0.20 | 1.5 1.5 1.5 1.7 1.7 | 14.5 15.5 16.5 18.5 22.0 | 17.0 18.0 19.0 22.0 25.5 | 0.013 0.011 0.010 0.010 0.009 | 341 420 495 658 948 |
| 24×0.5 24×0.75 24×1.0 24×1.5 24×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 0.20 0.20 0.20 0.20 0.20 | 1.5 1.5 1.7 1.7 1.7 | 16.5 18.0 19.0 21.5 26.0 | 19.5 20.5 22.0 25.0 29.5 | 0.013 0.011 0.010 0.010 0.009 | 416 512 623 809 1175 |
| 27×0.5 27×0.75 27×1.0 27×1.5 27×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 0.20 0.20 0.20 0.20 0.25 | 1.5 1.5 1.7 1.7 1.7 | 17.0 18.0 19.5 22.0 26.5 | 19.5 21.0 22.5 25.5 30.0 | 0.013 0.011 0.010 0.010 0.009 | 447 553 673 880 1317 |
| 30×0.5 30×0.75 30×1.0 30×1.5 30×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 0.20 0.20 0.20 0.25 0.25 | 1.5 1.7 1.7 1.7 1.7 | 17.5 19.0 20.0 23.0 27.5 | 20.5 22.0 23.5 27.0 31.0 | 0.013 0.011 0.010 0.010 0.009 | 481 614 728 984 1434 |
| 37×0.5 37×0.75 37×1.0 37×1.5 37×2.5 | 5 5 5 5 5 | 0.6 0.6 0.6 0.7 0.8 | 0.20 0.20 0.20 0.25 0.25 | 1.7 1.7 1.7 1.7 2.0 | 19.0 20.5 21.5 24.5 30.0 | 22.0 23.5 25.0 28.5 34.0 | 0.013 0.011 0.010 0.010 0.009 | 577 718 854 1162 1746 |