TABLE 1  TECHNICAL SPECIFICATION OF

CONDENSING STEAM TURBINES                  1-1

| No. | Designation & code Item Unit |  | 6MW | *25MW | 25MW | 50MW | **55MW |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Code |  | 78# | SX22# | 124# | 06# | 109# |
| 2 | Model |  | N6-3.43/435 | N25-0.98/270 | N25-3.43/435 | N50-8.83/535 | N55-8.83/535 |
| 3 | Type |  | Impulse tandem- comp.1-cylinder 1-exhaust | Impulse tandem- comp.1-cylinder 1-exhaust | Impulse tandem- comp.1-cylinder 1-exhaust | Impulse tandem- comp.1-cylinder 1-exhaust | Impulse tandem- comp.1-cylinder 1-exhaust |
| 4 | Rated output | MW | 6 | 25 | 25 | 50 | 55 |
| 5 | Max.output | MW |  | 30 | 30 | 55 | 60 |
| 6 | Speed | r/min | 3000 | 3000 | 3000 | 3000 | 3000 |
| 7 | Steam pres.before stop valve | Mpa | 3.43 |  | 3.43 +0.098 -0.196 | 8.83 | 8.83±0.49 |
| 8 | Steam temp.before stop valve | ℃ | 435 | 270 +10 -5 | 435 | 535 | 3.43 +5 -10 |
| 9 | Rated steam flow | t/h | 30 | 160 | 108 | 190 | 204/211(exhaust) |
| 10 | Max steam flow | t/h |  | 190 | 130 | 210 | 224 |
| 11 | Reheat steam temp. | ℃ |  |  |  |  |  |
| 12 | Exhaust steam temp. | Mpa | 0.0081 | Winter 0.049 Summer 0.0093 | 0.0044 | 0.0049 | 0.0056 |
| 13 | Cooling water temp. | ℃ | 27 | Win.60/Sum.26 | 20 | 20 | 20 |
| 14 | No. of stages |  | 1+8 | 1+8 | 1+8 | 1+8 | 1+8 |
| 15 | No. Of heaters |  | 1(HP heater) +1(deaerator) +1(LP heater) | 2(LP heater) deaerator and HP heater equip. | 2(HP heater) +1(deaerator) +1(LP heater) | 2(HP heater) +1(deaerator) +4(LP heater) | 2(HP heater) +1(deaerator) +3(LP heater) |
| 16 | Feed water temp. | ℃ | 165.3 | 128 | 175 | 222 | 215 |
| 17 | Heat rate | KJ/kW. H | 13060 | Winter 20879 Summer 16480 | 11087 | 9466 | 9488/9000 (exhaust) |
| 18 | Steam rate | Kg/kW.h | 5.02 | Winter 8.632 Summer 6.741 | 4.40 | 3.75 | 3.71 4.21(exhaust) |
| 19 | Last vane’s height | mm | 270 | 432 | 432 | 665 | 668 |
| 20 | Overall size (L x W x H) | m | 4.0x2.6x2.3 | 6.7x4.3x2.5 | 7.2x4.4x3.3 | 8.7xx6.9x3.4 | 9.48x6.96x3.5 |
| 21 | Turing wt. | T | 23 | 80 | 45 | 123 | 144 |
| 22 | Max.lifting wt. During erection | t |  | 21 | 18.7 | 40 | 27.5 |
| 23 | Cooling surface of condenser | m2 | 560 | 2600 | 2250 | 3500 | 3500 |
| Remark |  | - Operation at high pressure in winter, heat provided by cycle water. - 55MW condensing steam turbines, with not adjustable exhaust, exhaust pressure 0.981Mpa,exhaust capacity 30t/h. |  |  |  |  |  |

TABLE 1   TECHNICAL SPECIFICATION OF

CONDENSING STEAM TURBINES                  1-2

| No. | Designation & code Item Unit |  | *50MW | **75MW | 100MW | ***100MW | 125MW |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Code |  | 53# | 126# | 43# | 43A# |  |
| 2 | Model |  | N50-8.83/535 | N75-1.42/274 | N100-8.83/535 | N100-8.83/535 | N125-13.2/535/535 |
| 3 | Type |  | Impulse tandem- comp.1-cylinder 1-exhaust | Impulse tandem- comp.2-cylinder 2-exhaust | Impulse tandem- comp.2-cylinder 2-exhaust | Impulse tandem- comp.2-cylinder 2-exhaust | Impulse tandem- comp.2-cylinder 1-exhaust |
| 4 | Rated output | MW | 50 | 75 | 100 | 100 | 125 |
| 5 | Max.output | MW | 55 | 78.5 | 112 | 112 | 135 |
| 6 | Speed | r/min | 3600 | 3000 | 3000 | 3000 | 3000 |
| 7 | Steam pres.before stop valve | Mpa | 8.83 | 1.42 | 8.83 | 8.83 | 13.2 |
| 8 | Steam temp.before stop valve | ℃ | 535 | 274 | 535 | 535 | 535 |
| 9 | Rated steam flow | t/h | 193 | 386 | 370 | 360 | 379 |
| 10 | Max steam flow | t/h | 213 | 405 | 417 | 420 | 420 |
| 11 | Reheat steam temp. | ℃ |  |  |  |  | 535 |
| 12 | Exhaust steam temp. | Mpa | 0.0049 | 0.0054 | 0.0049 | 0.0047 | 0.0064 |
| 13 | Cooling water temp. | ℃ | 20 | 20 | 20 | 20 | 25 |
| 14 | No. of stages |  | 1+17 | 6 | 1+14+5x2 | 1+16+5x2 | 1+11+14 |
| 15 | No. Of heaters |  | 2(HP heater) +1(deaerator) +3(LP heater) | 1(LP heater) . | 2(HP heater) +1(deaerator) +4(LP heater) | 2(HP heater) +1(deaerator) +4(LP heater) | 3(HP heater) +1(deaerator) +3(LP heater) |
| 16 | Feed water temp. | ℃ | 220 | 60 | 227 | 231 | 248 |
| 17 | Heat rate | KJ/kW. H | 9400 | 13860 | 9254 | 8835 | 8223 |
| 18 | Steam rate | Kg/kW.h | 3.85 | 5.15 | 3.69 | 3.60 | 3.03 |
| 19 | Last vane’s height | mm | 610 | 1000 | 665 | 668 | 855 |
| 20 | Overall size (L x W x H) | m | 8.1x6.9x3.4 | 8.0x7.7x3.4 | 14x6.9x4.7 | 14x6.9x4.7 | 13.5x7.8x5.5 |
| 21 | Turing wt. | T | 113 | 95 | 256 | 260 | 300 |
| 22 | Max.lifting wt. During erection | t | 40 | 50 | 65 | 66 | 70 |
| 23 | Cooling surface of condenser | m2 | 3500 | 10000 | 6815 | 7000 | 5600 |
| Remark |  | - Operation at high pressure in winter, heat provided by cycle water. - 55MW condensing steam turbines, with not adjustable exhaust, exhaust pressure 0.981Mpa,exhaust capacity 30t/h. |  |  |  |  |  |

TABLE 1   TECHNICAL SPECIFICATION OF

CONDENSING STEAM TURBINES                  1-3

| No. | Designation & code Item Unit |  | *50MW | **125MW | ***100MW | ****200MW | *****200MW |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Code |  | SX26# | G18# | G03# | G01# | G02# |
| 2 | Model |  | N50-8.83/535 | N125-13.2/535/535 | N100-8.83/535 | N200-12.7/535/535 | N200-12.7/535/535 |
| 3 | Type |  | Impulse tandem- comp.1-cylinder 1-exhaust | Impulse tandem- comp.2-cylinder 2-exhaust | Impulse tandem- comp.2-cylinder 2-exhaust | Impulse tandem- comp.3-cylinder 2-exhaust | Impulse tandem- comp.3-cylinder 1-exhaust |
| 4 | Rated output | MW | 50 | 135 | 102 | 217 | 217 |
| 5 | Max.output | MW | 60 | 144 | 115 | 228 | 228 |
| 6 | Speed | r/min | 3000 | 3000 | 3000 | 3000 | 3000 |
| 7 | Steam pres.before stop valve | Mpa | 8.83 | 13.24 | 8.83 | 12.7 | 12.7 |
| 8 | Steam temp.before stop valve | ℃ | 535 | 535 | 535 | 535 | 535 |
| 9 | Rated steam flow | t/h | 190 | 389 | 370 | 610 | 610 |
| 10 | Max steam flow | t/h | 220 | 420 | 417 | 680 | 680 |
| 11 | Reheat steam temp. | ℃ |  | 535 |  | 535 | 535 |
| 12 | Exhaust steam temp. | Mpa | 0.0049 | 0.0049 | 0.0049 | 0.0049 | 0.0049 |
| 13 | Cooling water temp. | ℃ | 20 | 20 | 20 | 20 | 20 |
| 14 | No. of stages |  | 1+21 | 1+8+10+2x6 | 1+14+2x5 | 1+11+10+2x5 | 1+11+10+2x5 |
| 15 | No. Of heaters |  | 2(HP heater) +1(deaerator) +4(LP heater) | 2(HP heater) +1(deaerator) +4(LP heater) | 2(HP heater) +1(deaerator) +4(LP heater) | 3(HP heater) +1(deaerator) +4(LP heater) | 3(HP heater) +1(deaerator) +4(LP heater) |
| 16 | Feed water temp. | ℃ | 220 | 239 | 225 | 245 | 245 |
| 17 | Heat rate | KJ/kW. H | 9043 | 8094 | 9085 | 8164 | 8163 |
| 18 | Steam rate | Kg/kW.h | 3.80 | 2.89 | 3.62 | 2.811 | 2.811 |
| 19 | Last vane’s height | mm | 668 | 668 | 668 | 668 | 668 |
| 20 | Overall size (L x W x H) | m | 8.65x6.9x3.4 | 13.5x7.4x5.4 | 14x7.0x4.7 | 18.3x7.0x5.9 | 18.3x7.0x5.9 |
| 21 | Turing wt. | T | 140 | 325 | 256 | 490 | 490 |
| 22 | Max.lifting wt. During erection | t | 40 | 70 | 65 | 78 | 78 |
| 23 | Cooling surface of condenser | m2 | 3500 | 7500 | 6815 | 11220 | 11220 |
| Remark |  | *The alteration of old 50MW(06#) **The LP cylinder alteration of old 100MW(43#), the full iteration is 43A# ***The alteration of old 125MW (up steam type) ****The alteration of old 200MW(34#) *****The alteration of old 200MW(55#) |  |  |  |  |  |