| V94.3a Annexure “A” Specification FOR 600 KVA GAS GENERATOR. |  |  |  |  |
| --- | --- | --- | --- | --- |
| Date: |  |  |  |  |
| 07-09-2006 |  |  |  |  |
|  | Approved By: |  |  |  |
|  | Checked By: |  |  |  |
|  | Prepared By: |  |  |  |
|  | Process and Plants Department. |  |  |  |

- Scope

This specification cover the minimum requirements for the design, materials, construction, testing and inspection, and performance of factory assembled packaged continuous duty Gas Engine Driven Generator Set.

The generator shall be suitable for parallel operation with similar or other generators having same or different capacities. The generator package be consist of gas engine, generator, weather protective enclosure, control panel and other associated items and equipment necessary for the proper operation of the equipment as a complete package.

The bidder must fill the Data Sheet at Appendix-I. The bidder is required to submit a P&ID diagram showing all equipment.

The following manufacturer will be acceptable:

### i) Cummins, mtu  for Engine

ii) Waukesha, Caterpillar, Stamford, Siemens, Magna Max for alternator

- Reference Standards & Codes

The equipment and material selection, design, manufacturing, testing and inspection shall confirm to the latest editions of the followings relevant codes and standards. Any changes and alterations and necessary re-certification of the equipment for compliance with the applicable codes and standards requirements shall be at the expense of the contractor.

- International Electro Technical Commission (IEC).

- American National standard Institute (ANSI)

- National Electrical code (NEC).

- International Organization for standardization (ISO).

- Institute of Electrical & Electronics Engineers (IEEE)

- National Electrical Manufacturing Association (NEMA)

- API-RP500A for classification of Areas for Electrical installation in Petroleum Refineries.

- DESIGN Ambient Conditions

- Design Maximum Ambient Temperature, °F			112

- Design Minimum Ambient Temperature, °F			30

- Temperature for Thermal Rating of Air coolers, °F		115

- Maximum Wet Bulb Temperature for Thermal Rating		88	 of Evaporative Air cooler, °F

- Control Room Temperature (Minimum) °F		64.4

- Control Room Temperature (Maximum) °F		75-86

- Control Room Temperature (Mean Average) °F		75

- Switch Gear Room (Minimum) °F			64.4

- Switch Gear Room (Maximum) °F			75-85

- Design Wind Velocity, (Mile/Hr)				100

- Atmosphere				         Mountainous & Windy

- CLIMATIC CONDITION

- Relative Humidity (Minimum Monthly Average)	27%

- Relative Humidity (Maximum Monthly Average)	61%

- Altitude, ft (Above Mean Sea Level)			1900

- Dry Bulb Temperature (Maximum), °F			112

- Dry Bulb Temperature (Minimum), °F			30

- Average Barometric Pressure				13.8 psia

- Ice/Snow							None

- Climate							Hot Humid

- SEISMIC DESIGN DATA

Zone 2B, Upper Moderate with ground acceleration of 0.2

- AREA CLASSIFICATION

Area with the package battery limits in Class I, Div. I, Group D as defined by              API RP-500. Remaining area with the package limit is Class I, Div. 2, Group D.

- Rating

The Generator set shall be designed in accordance with the followings:

Class  			:	Continuous Rating

Rated Out put 		:	600 KVA

Rated Voltage		:	400 V + 5%

Phases			:	3

Frequency 		:	50 Hz.

Power Factor 		:	0.8

Overload:	10% for one hour following 100% load in. 12- hour operation

- Gas composition (MELA PLANT)

The composition of gas to be used as fuel gas for generator at site is as under:

| Component | ## Mole (%) |
| --- | --- |
| Methane C1 | 85.0342 |
| Ethane C2 | 7.7791 |
| Propane C3 | 3.0976 |
| Iso-butane i-C4 | 0.4617 |
| n-butane n-C4 | 0.7406 |
| Iso-pentane i-C5 | 0.2150 |
| n-pentane n- C5 | 0.1723 |
| Hexane + C6+ | 0.1427 |
| Carbon dioxide CO2 | 1.2392 |
| Nitrogen N2 | 1.1176 |
| Hydrogen Sulphide H2 S | NIL |
| Specific Gravity | 0.6686 |
| Calorific Value BTU/Cuft | 1139.66 |

- Gas composition (CHANDA PROJECT)

The composition of gas to be used as fuel gas for generator at site is as under:

| Component | ## Mole (%) |
| --- | --- |
| Methane C1 | 82.1300 |
| Ethane C2 | 7.8964 |
| Propane C3 | 3.1264 |
| Iso-butane i-C4 | 0.3256 |
| n-butane n-C4 | 0.5007 |
| Iso-pentane i-C5 | 0.0722 |
| n-pentane n- C5 | 0.0238 |
| Hexane + C6+ | 0.1427 |
| Carbon dioxide CO2 | 4.2444 |
| Nitrogen N2 | 1.6231 |
| Specific Gravity | 0.6870 |
| Calorific Value BTU/Cuft | 1084.31 |

- Gas-Engine

The Gas-Engine shall be capable of developing sufficient horsepower to drive the alternator on full load. The engine shall be naturally aspirated / turbo-charged, water-cooled complete with all auxiliaries and shall be designed for most suitable number and layout of cylinders. The engine be provided with thermocouples/temp sensors for monitoring of each cylinder temperature.

The Gas-Engine shall be designed, manufactured and tested in accordance with the requirements of relevant section of power generation application. The engine shall be in compliance with BS 5514/ISO 3046 or equivalent.

All auxiliaries of the engine must be genuine as per approved vendors of engine manufacturer unless specified.

6.1      Cooling System

A gear driven centrifugal pump shall circulate water through a radiator, cooled by a fan. Radiator fan shall be belt driven from the engine crankshaft. The cooling system shall provide automatic control of the engine inlet water temperature. Thermostatically mounted bypass valves shall be arranged so that cooling water flow cannot be shut-off.

The cooling system shall also be including:

- Thermocouples for pre-alarm and trip mounted in suitable points.

- Coolant level switches suitable for local and remote indication.

- Pressure gauge mounted on cooling water pump delivery.

6.2       Engine Lubrication System

The engine shall be supplied with a complete pressure lubrication system, which shall include the following equipment:

- Shaft driven positive displacement oil pump with pressure relief valve.

- Oil cooler with thermostatically controlled bypass valve.

- An integral oil reservoir with level indication, oil filter, vent and valve drain connection.

- Level switches for local and remote indication.

- Pressure and temperature gauges mounted on:

      - Lube Oil pump delivery pressure

      - Lube Oil filter (differential pressure)

      - Oil cooler water temperature.

6.3	Fuel Gas System

The engine shall be supplied with complete fuel gas system, which shall include as a minimum the following:

- Pressure reducing regulator to reduce line pressure of 100 psi.

2)    	Relief valve sized for max. output capacity of pressure reducing regulator based on maximum supply pressure and orifice installed in regulator.

- Fuel system manual block valve.

- Automatic valve in fuel system to shut-off fuel to the engine and vent engine side of fuel system when engine is shutdown.

- Gas filters.

6)        Flexible joints

6.4     Exhaust System

A standard type silencer complete with companion flanges, and flexible stainless steel exhaust pipe/fitting properly sized shall be furnished and installed according to the manufacturer’s recommendation. Exhaust pipe size shall be sufficient to ensure that exhaust backpressure does not exceed the maximum limitations as specified by the engine manufacturer.

6.5  	Starting System

A DC electric starting system powered by batteries with positive engagement shall be furnished. The motor voltage shall be as recommended by the engine manufacturer.

Batteries-A lead-acid batteries set compatible with the starting system complete with all necessary cables and clamps shall be provided. Batteries shall have capacity for at least 6 consecutive starts.

Battery Trays – Battery trays shall be provided for the batteries. It shall treat to be resistant to deterioration by battery electrolyte. Further, construction shall be such that any spillage or boil-over battery electrolyte shall be contained within the tray to prevent a direct path to ground.

6.6  	Governor

Mechanical or Electronic type governor maintaining engine speed within specified shall be provided to protect the engine against over speed and under speed. The governor shall regulate the genet to meet the load variation and under steady state conditions the governor shall hold the frequencies within + 0.25%. Under transient conditions the governor shall hold the frequency within + 2.5 Hz and recover within 2 seconds.

- ALTERNATOR

  - The alternator shall be of 4-pole, 1500 RPM, 50 Hz, 400 V, 300 KVA, brushless excitation, air-cooled and weather protected. Design, construction and performance of the generator shall conform to the requirements of IEC 60034.

  - The stator windings shall be Y- connected for power output. The rotor shall be constructed with the armature field and the brush less exciter assembly on a common shaft.

  - The alternator shall be able to carry the unbalanced load of any magnitude up to the rated current for each phase.

  - An automatic voltage regulator shall be provided to allow + 5% variation of the rated voltage. When the utilization is quickly switched from no load to full load, the voltage shall not deviate by more than 20% during 0.5 second.

  - The excitation system shall be rated to cover field-forcing condition during step loading and system electrical faults.

  - The generator shall be suitable for parallel operation. The characteristics of the generators shall allow them to share active and reactive loads under stable conditions from zero to full load.

  - The insulation of generator and exciter shall be Class F (min.). All insulation materials shall be chosen for maximum moisture, fungus, abrasion and corrosion resistance, as well as high dielectric strength and high bonding qualities.

  - The output signal shall be practically sinusoidal, and the characteristics of the waveform shall be in accordance with BS-4999, Part-40

  - The alternator shall not create radio electric disturbances in particular by injection of eddy current frequencies in the line.

  - The short circuit ratio referred to the rated voltage at saturated condition shall not be lower than 0.78.

  - Field forcing capability shall be sufficient to maintain 3 times the generator full-load current for ten seconds to enable adequately graded relay settings for system fault current protection.

- COUPLING

Engine and alternator shall be coupled by means of a non-lubricated, lightweight, failsafe type flexible coupling to provide the drive and absorb the transmission of shock loads.

- SKID & ENCLOSURE

The entire Gas Generator package with all accessories shall be mounted on a skid. The package should be provided with weather proof enclosure mounted on the skid for its safety to resist the dust, rain, wind and thunderstorm. The enclosure will be designed in away that no resistance will be occurred for generator operation, access to panel and routine maintenance jobs.

Lifting eyes shall be provided at an appropriate location for the balanced lifting of skid with crane. Provision for properly sized anchor bolts shall be left on the structure of power skid frame.

- CONTROL PANEL

Generator set shall be provided with a remote control panel. The control panel shall be sheet, self-supporting type suitable for floor mounting, ready wire type, complete of base frame to be embedded in the floor. The class of protection shall be IP54.

The Control panel shall equipped with Bus-bar system for supply & auxiliaries, all protective devices and controls (alarming and tripping), starting/stopping sequence control, load ramping control, excitation controls, monitoring equipments and emergency stop push-button. An engine, alternator or system fault shall trip the generator circuit breaker.

The panel will be installed in a separate control room 60 meters away from the generators. All necessary cables (preferably armored) shall be provided with the panel for its connection with the Gen-set.

All necessary control panel supply should be provided through AC/DC converter from bus bar/outer source with batteries back-up.

The board shall contain in separate compartments the following system.

  - Bus bars system for mains and auxiliary services.

  - Control systems:  Control and signalization system of each set and its auxiliaries which shall include following controls with automatic/manual selection:

  - Start/stop control.

  - Load/Speed Regulation control.

  - Excitation/AVR Control

  - Synchronization (to run the gen-set in parallel with similar or different generator set)

  - Protection System: The protection system should be supplied with the panel to protect the Generator against unusual circumstances. All the protections must trip the circuit breaker, Gas engine Shut-Down and closing of fuel gas supply valve automatically. The protection system should have following equipments/protection systems:

  - Motor rechargeable spring operated circuit breaker suitable for generator rating & 400V, 50Hz operation. The circuit breaker should have manual recharging option too.

  - On-Off push buttons for open/close the circuit breaker and relevant signal lamps.

  - Emergency Stop Push Button.

  - Generator Over current Protection.

  - Reverse Current Protection.

  - Generator over/under voltage Protection.

  - Excitation over-current Protection.

  - Excitation over-Voltage Protection.

  - Generator over speed Protection.

  - Stator/Rotor earth fault protection

  - Field failure relay.

  - Metering system shall include:

  - Ammeters with selector switch

  - Voltmeter with selector switch

  - KW meter

  - Frequency meter

  - Power factor indicator

  - KWH meter

  - Temperature indicators (each cylinder, coolant, stator & rotor winding etc)

  - Elapser/Hour Counter

  - Alarm system should consist of annunciator panel with block signal lamps for warnings, faults and any abnormality in the gen-set and shall include:

  - High temperature of cooling water

  - High cooler temperature

  - Low pressure of lubricating oil

  - Over speed

  - Failure of starting system

  - Lubricating oil filter differential pressure

  - Low pressure of fuel gas

  - High pressure of fuel gas

  - Low level of lubrication oil

  - Starter earth fault

  - Rotor earth fault

  - Field failure

  - Over current

  - Over load

  - Over voltage

  - High stator temperature

  - High bearing temperature

- SPARE PARTS

The vendor shall submit with the quotation comprehensive fully detailed schedules of spare parts with separate prices of each covering all equipment during construction/commissioning/start-up and 2 years operation. All spare parts supplied shall be new and fully interchangeable with the main equipment being supplied. The un-priced list of spare parts must be provided with technical bid for review.

These spare parts shall be delivered at the same time as the main equipment. The spare parts for start-up and operation shall be packed separately.

Note:  The spare parts for two-year operation will not be included in the financial evaluation.

The cost of start up spares and commissioning spares will be included in financial evaluation.

- OPERATION / SERVICES MANUALS.

The successful bidder will provide one set of the following literature with each of the Gas Generator Set supplied.

- Service, operation and Spare Parts				One Each

manual for Gas Engine.

- Service, operation and Spare Parts				One Each

manual for Alternator

- Complete circuit & logic diagrams for			One Each

Control Panel

- Service, operation and Spare Parts				One Each

manual for Control Panel.

- Manufacturer Data Records (MDR)				One Each

The above manuals should be provided along with the shipping document.

- TESTS & RECORDS

  - All the necessary tests and inspections should be carried out during manufacturing, each equipment and complete package.

  - The complete gas generator package of together with control panel shall undergo the performance test to verify the actual parameters with specifications.

  - The vendor shall record all test results and issue test certificates, which shell record all calculated parameters (e.g. reactance, efficiencies, etc.).

  - The packager/manufacturer should supply all the performance test records to purchaser along with shipping documents. The other test records during manufacturing/assembling should be provided to purchaser.

- COMMISSIONING

The vendor is required to arrange free of cost commissioning and start-up of generator at OGDCL field by their service engineer.

- AFTER SALES SERVICE

The manufacturer/ seller should have good established facilities in Pakistan for after sales service, maintenance cells and spare parts supply, the bidder should provide the proof of these facilities and OGDCL will have the right to visit these facilities prior to finalization of order.

- TOOLS

The bidder shall supply all necessary tools required for routine operation & maintenance with each generator. A list of the tools should be provided with the technical proposal. The price of tools will not be included in the financial evaluation.

- GUARANTEE

The Contractor shall guarantee that the equipment furnished is free from fault in design, workmanship, is of adequate size and capacity, and of proper material to satisfactorily fulfill the operating conditions specified. Should any defect in design, material workmanship or operating characteristics develop during the first year of operation, the contractor shall make all necessary alternations, repairs and replacements of defective equipment components at his own cost including transportation, installation and testing.

- SHIPPING

The material shall be properly conditioned for shipping against all possible damages. Contractor shall be responsible for shipment of equipment to Site and for the adequacy of the preparations for shipment ensuring that materials and equipment arrive at their destination in undamaged condition. All components shall be shipped simultaneously.

Contractor shall provide the Owner shipment details; dates of equipment departure and arrival at Site and a list of weights and sizes of shipment packages prior to dispatch.

- SUMMARY

| Sr. No. | Description | Unit | Quantity | Total Price (C & F) by Sea |
| --- | --- | --- | --- | --- |
| 01 | Gas Engine driven Generating Set Continuous Power 600 KVA @ 0.8 Power Factor at 500 C, 400 V, 3-Phase, 50 Hz at 1500 RPM with all accessories (As per details of this specification) | Set | As per indent |  |
| 02 | Floor standing control panel & Instrumentation | No | As per indent |  |
| 03 | Gas street comprising of gas regulator, coalescing filters, solenoid valve & flow meter | No | As per indent |  |
| 04 | 2-years recommended spares. | Set | As per indent |  |
| 05 | Tools for O&M | Set | As per indent |  |

Appendix-I

DATA SHEET

| Sr.# | Description | OGDCL Requirement | Bidder Input |
| --- | --- | --- | --- |
| 1 | Rating Parameters (Gen Set) |  |  |
|  | Model | By vendor |  |
|  | Continuous power kVA (Standard) | Vendor to give de-rating profile with temp. & altitude. |  |
|  | Power Factor | 0.8 |  |
|  | Voltage Volts | 400 ± 5% |  |
|  | Frequency Hz | 50 ± 1% |  |
|  | Speed RPM (Maximum) | 1500 |  |
|  | Overload | 10% for 1 hour following 100% load in 12 hour operation |  |
| 2 | Ambient conditions |  |  |
|  | Ambient Temp degree F | 112 |  |
|  | Relative humidity | 61% Maximum |  |
|  | Altitude (ft.) | 1900 ft |  |
| 3 | Gas Engine |  |  |
|  | Make | Cummins, Cater Pillar, Waukesha |  |
|  | Model | Vendor to specify |  |
|  | Prime power | Vendor to specify de-rating profile with respect to altitude. |  |
|  | Speed regulation | Governor |  |
|  |  | ± 0.25% of 50Hz at steady Load Condition |  |
|  | Aspiration | Natural/Turbo Charge |  |
|  | Fuel consumption | on full load of Prime Operation |  |
|  | Fuel Gas System | Meet the gas specification at Article 5.0 |  |
|  |  | Regulator | Specify range |
|  |  | Gas Inlet Block Valve (Manual) |  |
|  |  | Gas Inlet Block Valve (Automatic) |  |
|  |  | Gas filter |  |
|  | Engine Cooling System | Water Cooling with Radiator |  |
|  |  | Coolant Level Sensors |  |
|  |  | Coolant Temperature sensors |  |
|  |  | Thermostatic control valve |  |
|  | Engine Lube Oil System | Pressure Lubricating System |  |
|  | Exhaust Control System | Standard type Silencer Complete with Flexible coupling and complete accessories. |  |
|  |  | Sensors for each cylinder temperature |  |
|  |  | Euro-I |  |
| Sr.# | Description | OGDCL Requirement | Bidder Input |
|  | Starting System | DC Starting System for at least 6 consecutive starts |  |
|  |  | Batteries |  |
|  |  | Battery Trays |  |
| 4 | Alternator |  |  |
|  | Make | Stamford, Siemens, Waukesha, Cummins, Perkins. |  |
|  | Design | Self cooled |  |
|  | Standard | IEC-60034 |  |
|  | Insulation class | Min. F |  |
|  | No. of Poles | 4 |  |
|  | Cooling System | Air Cooled |  |
|  | Voltage Regulation System | Solid State AVR with ± 5% variation in rated voltage |  |
|  | Excitation Type | Brushless Excitation |  |
|  | Stator | Y-Connection (Out put) |  |
|  | Rotor | 4-pole field winding with brushless excitation |  |
| 5 | Control Panel & Instrumentation |  |  |
|  | Bus -Bar | Mains Connection |  |
|  |  | Auxiliaries Connection |  |
|  | Controls | Manual/Automatic Control Switch |  |
|  |  | Start/Stop sequence control |  |
|  |  | Speed/Load Regulation |  |
|  |  | AVR Control |  |
|  |  | Excitation |  |
|  |  | Synchronization |  |
|  | Protection | 4-pole Circuit Breaker |  |
|  |  | Emergency Stop Push Button |  |
|  |  | Reverse Current Protection |  |
|  |  | Over Current Protection |  |
|  |  | Over/under voltage protection |  |
|  |  | under/over Excitation Protection |  |
|  |  | Over speed Protection |  |
|  |  | Field Failure Protection |  |
|  | Metering | Voltmeter, Ammeter |  |
|  |  | Hour counter meter/Elapser |  |
|  |  | KW, KVAR, PF, KWH meter |  |
|  |  | Frequency meter |  |
|  |  | Temperature Displays (cylinder, exhaust, winding, oil, coolant) |  |
|  |  | Pressure Displays ( |  |
|  | Alarms/Warnings | Alarm/Horn |  |
|  |  | Block Signal lamp indications |  |

| Sr.# | Description | OGDCL Requirement | Bidder Input |
| --- | --- | --- | --- |
| 6 | Skid & Enclosure | Weather Proof Enclosure Mounted on Skid Frame |  |
| 7 | Warranty | 12 month from commissioning |  |
| 8 | Commissioning | On site |  |
| 9 | Spare Parts | Two years operation |  |
| 10 | Tools | Complete set of special tools for handling and maintenance of Gen Set |  |
| 11 | After sale services in Pakistan | Plz. Mention local address |  |
| 12 | Drawing and Data | O&M, Service and Parts manual for each Gen set with shipment |  |
| 13 | Delivery Period | 4 to 6 Months (Maximum) |  |
|  | Notes: |  |  |
| i | All the columns of the data sheets must be filled by the bidder with brief information. Only yes or comply is not appropriate. |  |  |
| ii | Please attach additional supporting literature for verification of data (OEM Published) |  |  |
| iii | Packager Should Provide OEM Authority letter of Engine & Generator for manufacturing/assembling of Generator Set. |  |  |
| iv | The OEM of the selected equipment should provide the certificate showing the 7 years experience for manufacturing like Generator, Engines and Couplings. |  |  |