Proposal of the Seawater desalination 
埃及海水淡化工程方案设计
1. Project Name工程名称
NEW TECHNOLOGY CO-GENERATION POWER DESALTION PLANT(CPDP)
中东欧电力和水项目公司新技术电力和海水淡化水共生厂
2. Project Location 工程地点

3. Available Site Area：可用占地面积
12.5ha（250mx500m）for first phase, 25ha for the second phase.
4. Project contents and scale 工程内容和规模

4.1 Product water for the first phase（2011） is 360000m3/d and 600000m3/d （2015） for the second phase.  36万m3/d海水淡化（2011）；60万m3/d（2015）
4.2 The scale for bottled water is 3000m3/d     3000m3/d瓶装饮用水
4.3 crystallized salt product  配套结晶盐项目

According to the client requirement, this part is included in another project, so this cost is not in the offer of this project.
根据业主要求，此部分另外立项考虑，投资不在本次报价范围内
5. The raw seawater quality 进水水质情况 
5.1 Water Quality at the Project Location Physico-chemical Analysis of Water Samples at the Project Location (Samples Delivery Date: 29 June 2008) 
项目地点处水质情况如下（采用点时间为2008年6月29日）
	Parameters

参数
	Unit
	Concentration

	
	
	Site 1
	Site 2
	Site 3
	Site 4
	Site 5

	pH 
	-
	8.0
	7.9
	8.0
	8.0
	7.8

	Water Temperature水温 
	oC
	23
	24.5
	25
	24
	26

	Electrical Conductivity 

电导率
	μmho/cm
	61150
	59800
	62000
	59200
	60500

	Transparency
透明度 
	cm
	90
	90
	90
	90
	90

	Total Dissolved Solids 
	mg/I
	39503
	39557
	38795
	38889
	39084

	Suspended Solids 
	mg/I
	8.6
	9.5
	10.6
	10
	8.9

	Total Solids 
	mg/I
	39511.6
	39566.5
	38791.6
	38899
	39092.9

	Total Alkalinity (as CaCO3) 
	mg/I
	120
	122
	124
	128
	116

	Chloride(CI-) 
	mg/I
	25000
	25000
	25000
	25000
	24000

	Sulfate
 (SO4 2-) 
	mg/I
	421
	412
	439
	432
	438

	Nitrate (NO3-N) 
	mg/I
	0.02
	0.01
	0.01
	0.01
	0.01

	Sodium (Na+) 
	mg/I
	11502
	10842
	10912
	10987
	10223

	Potassium (K+) 
	mg/I
	753
	731
	692
	684
	613

	Manganese 
	μg/l
	Nil
	0.02
	0.27
	0.65
	0.11

	Calcium (Ca2+) 
	mg/I
	561
	641
	561
	561
	601

	Magnesium (Mg2+) 
	mg/I
	1703
	1654
	1605
	1654
	1581


Notes:  (1) 100 m up stream.  水质采用点上游100米处，(2) 200 m up stream.  水质采用点上游200米处

(3) fronting the power plant site. 水质采用点厂址前，(4) 100 m down stream.     水质采用点下游100米处，(5) 200 m down stream.     水质采用点下游100米处
5.2 Surface Water Quality at 300, 500 and 700 m in Three Profiles Extending Seaward form the Project Site (Hydraulics Research Institute, EDF Suez Gulf Power S.A.E., 2000)
项目地点向海延伸300m，500m，700m处的表面水质情况：

	Parameter
	Range
	Average

	Temperature,  oC
	17-18 
	17.3

	Salinity,  % 盐分
	42.17-42.69 
	42.36

	DO,   mg/l
	4.88-7.57 
	7.06

	DOM,  mgO2/I
	0.36-2.02 
	1.47

	pH
	8.90-8.2 
	8.12

	TSM,   mg/l
	16-30.7 
	18.9

	Chl – a,  mg/l
	0.11-0.23
	0.20

	NH4,  μmole
	0.1-2.4 
	0.75

	NO2,  μmole
	0.026-0.78 
	0.24

	NO3,  μmole
	0.003-0.248 
	0.128

	TN,    μmole
	1.58-11.66 
	6.20

	PO4,  μmole
	0.055-0.11 
	0.069

	TP,    μmole
	0.26-0.77 
	0.48

	SiO4, μmole
	1.81-2.38 
	2.00


5.3 Water Quality at the Project Location Organic Analysis of Water Samples at the Project Location (1) (Samples Delivery Date: 29 June 2008)
五处采样点水质的有机物分析情况

	Parameters
	Unit
	Concentration

	
	
	Site 1
	Site 2
	Site 3
	Site 4
	Site 5

	COD
	mgO2/I
	32
	28
	32
	28
	30

	BOD
	mgO2/I
	16.2
	16.5
	18
	7.8
	24.9

	Oil& Grease
	mg/I
	14.8
	15.1
	15.3
	16.5
	16.0

	Phenol 石碳酸
	mg/I
	N/D(2)
	N/D
	N/D
	N/D
	N/D

	Polycyclic Aromatic Hydrocarbons
多环芳烃化合物
	
	0.041
	0.039
	0.037
	0.038
	0.0375

	Total Hydrocarbons
总氢碳化合物
	
	78.6
	79.2
	81.6
	85.7
	84.3

	Chlorinated Hydrocarbons 
氯化烃
	
	0.034
	0.049
	0.053
	0.047
	0.062

	Polychlorinated Biphenyles (PCBs) 多氯联苯
	
	0.67
	0.87
	0.85
	0.76
	0.68


Notes:   (1) The same sampling points as indicated in Notes of （1）
(2) ND = Not Detected.

5.4 Heavy Metals Analysis of Water Samples (1)

(Samples Delivery Date: 29 June 2008) 水样的重金属分析

	Parameters
	Unit
	Concentration
	Detection Limits (2)

	
	
	Site 1
	Site 2
	Site 3
	Site 4
	Site 5
	

	Zinc 锌
	mg/I
	N/D(3)
	N/D
	N/D
	N/D
	N/D
	0.005

	Cadmium 镉
	mg/I
	0.162
	0.158
	0.151
	0.142
	0.14
	0.002

	Chromium 铬
	mg/I
	0.096
	0.089
	0.091
	0.092
	0.093
	0.02

	Lead 铅
	mg/I
	1.063
	1.034
	1.048
	1.052
	1.051
	0.05

	Nickel 镍
	mg/I
	0.676
	0.669
	0.668
	0.672
	0.674
	0.02


Notes:  (1) The same sampling points as indicated in Notes of Table（1）

 (2) Detection Limits: The sensitivity of the equipment.          
(3) ND = Not Detected.

5.5 Microbiological Analysis of Water Samples(1)  (Samples Delivery Date: 29 June 2008) 

水样的微生物分析
	Site No.
	Total Bacterial Counts, Cell/cm3
	Most Probable Number Index / 100mI

	
	At 22 oC
	At 37 oC
	Total Coliform
总大肠杆菌
	Faecal Coliform

粪大肠杆菌

	Site 1
	64
	72
	1.1 x 102
	70

	Site 2
	51
	54
	1.4 x 102
	70

	Site 3
	59
	64
	70
	30

	Site 4
	4
	2
	N/D (2)
	N/D

	Site 5
	3
	2
	N/D
	N/D


Notes:    (1) The same sampling points as indicated in Notes of Table (1). 
(2) N/D = Not Detected

5.6 Algal Counts of Water Samples (*) 

 (Samples Delivery Date: 29 June 2008) 水样的含藻类统计
	Parameters
	Count (Organisms/ml)

	
	Site 1
	Site 2
	Site 3
	Site 4
	Site 5

	Diatoms 硅藻类
	120 
	100 
	90 
	110 
	110 

	Green Algae 绿藻类
	10 
	10 
	10 
	10 
	10 

	Blue-Green Algae
蓝藻类
	20 
	20 
	10 
	10 
	10 

	Total Algal Counts
总藻类
	150 
	130 
	110 
	140 
	140 


 Notes: (*) The same sampling points as indicated in Notes of （1）.
5.6 Water Quality Assessment And Our Advice 海水水质评价和建议

According to the seawater quality measurement and data (if right, verified), the seawater of this area contains oil, organics, heavy metal ion, and these materials contents have a high percentage. If intake such seawater, it will increase the investment, cost and maintains of the seawater desalination plant, and as the same as the electric power plant. Therefore, our advices as follows:
1. Please verify the position of the sampling points, detect measurements and data record. We will also coordinate with your part to this work after sign the agreement.
2. If the data is exactly correct, the advice of altering the sample points or project site is much better.  
根据上述海水水质检测数据（如果合适、无误），该处海水中油、有机物、重金属含量过高，如果取用这样的海水，不仅会增加海水淡化厂的投资、成本以及日常维护量，对电厂部分也是同样的。因此，我方建议：

1. 请核实取水点位置、检测方法、数据记录等。协议签署后我方也会配合进行该工作。
2. 如果数据无误，建议本工程最好更换取水点或厂址。
6. The requirement of product quality产品质量要求
6.1 Desalination seawater product: with the following specifications
脱盐海水产品的水质要求如下：
	Anions
	PPM
	CATIONS
	PPM

	Bicarbonate重碳酸盐
	27
	Sodium钠离子
	10 -12

	Sulphate硫酸盐
	50
	Calcium钙离子
	3 - 4

	Chloride氯化物
	47
	Magnesium镁离子
	19

	Nitrate硝酸盐
	0 - 4
	Potassium钾离子
	0.1 - 0.2

	TDS (mg/l)
	130
	T. Hardness 硬度
	50

	pH
	7.8 – 8.0
	
	


6.2 Bottled drinking water with 250 ml, 500 ml, 1500 ml, 1 gallon, 6 gallons PET packaging with the following specifications: 产品瓶装水的水质要求如下：
	Anions
	PPM
	CATIONS
	PPM

	Bicarbonate重碳酸盐
	50
	Sodium钠离子
	12

	Sulphate硫酸盐
	50
	Calcium钙离子
	15

	Chloride氯化物
	15
	Magnesium镁离子
	5

	Fluoride氟化物
	0.8
	Potassium钾离子
	0.2

	Nitrate硝酸盐
	0.1
	Iron铁离子
	0.02

	TDS (mg/l)
	110
	T. Hardness硬度
	50

	pH
	7.0
	
	


7. Introduction of the Process 工艺介绍
The methods of seawater desalination are thermo method and membrane method as mechanism. Nowadays, the project of seawater desalination mainly has three techniques: MSF, MED and MVC. Membrane methods is referring to the SWRO techniques, which utilize semi permeable membrane, under a certain pressure it just allows the water permeate and then separate the impurity from the seawater. SWRO has become to the main techniques in the field of membrane techniques. thermo method is referring to the MED techniques, which is a main technique in the field of thermo method. 
海水淡化的方法按脱盐机理可分为热法和膜法，实用化的热法海水淡化工艺的主要有：多级闪蒸(MSF)、低温多效(MED) 和压汽蒸馏(MVC)三种技术。膜法主要指海水反渗透（SWRO）技术，它利用半透膜，在压力下允许水透过而使盐分和杂质截留的技术。其中低温多效（MED)已成为热法的主流技术，海水反渗透（SWRO）已成为膜法的主流技术。
There are two problems in the process of thermo method of seawater desalination, one is the decay of the equipment, and the other is scaling on the heat-transfer pipe. To solve these two problems, widely used method is to use the corrosion-resistant alloy, and added the antisludging agent to the intake seawater. In addition, due to the corrosion and scaling velocity of the seawater and brine is related to the evaporation temperature, so in the field of seawater desalination to decrease the evaporation temperature of the seawater is a most important problem. This is why MED technique is rising in past dozens of years. A MED technique is generally operated in 70 centi degree, in this temperature, when enrichment factor of seawater is 1.8~2.0, denuded zone of the calcium sulphate and carbonate is still removed from operating point, so the scaling probability is minimum. also because of the use of aluminium alloy, epoxy coating, plastic, which is corrosion-resistant in this temperature, so MED equipment can be added only minimum antisludging agent to the seawater, not like MSF, which should be added acid to remove the CO2 and O2. So it can reduce the cost of investment and maintains. Therefore, in past few years, MED technique develops fast, and until 2001, MED separate unit can reach a water yield of 68000m3/d. Also, the total volume of process water is exceeding to the MSF technique, and there are many operation outstanding achievements in the worldwide, and the technique has maturely used in the world.
热法海水淡化工艺面临的两大问题是设备的腐蚀和海水在传热管上的结垢。为了克服这两个难题，广泛采用的办法是使用贵重的耐蚀合金、在进料水中加入阻垢分散剂。另外，由于海水和浓盐水的腐蚀和结垢速度与其蒸发温度密切相关，在海水淡化领域也把降低海水的蒸发温度作为解决问题的突破口，这就是近十几年来兴起的低温淡化（MED)技术。低温多效蒸馏（MED)一般在70 ℃以下进行操作，在这个温度下，海水的浓缩倍数为1.8～2时，硫酸钙和碳酸盐的结晶析出区还远离操作点，所以结垢倾向极小。又因铝合金、环氧树脂涂层、塑料的使用在该温度下能耐氧的腐蚀，因此低温多效蒸馏装置对进入装置的海水只需加入微量阻垢剂，而不需像多级闪蒸装置那样加酸脱除CO2及O2，因而降低了投资和操作成本。因此，近几年低温淡化（MED)发展迅速，到2001年低温多效（MED)单台最大产水量已达到68000m3/d，其年总制水量也已超过MSF工艺，并在世界各地已由多台运行业绩，技术是成熟的。
The SWRO technique has many advantages, such as low project investment, short construction period, small scale of plant area, simply operation maintains, low energy, low cost of water yield. After use the measure of energy recycle device and improving the water recycle rate. the energy consumption is great reduced in one unit of water yield, the energy consumption of the desalination seawater is decreased from 4.0~5.5  kwh/m3 per ton now to the 2.5～4.5 kwh/m3 per ton. As the development in these years, SWRO technique is become much more maturely used, the production capacity of complete plant become much more powerful, the scale of project is much bigger. Therefore, the SWRO technique is become one of the main techniques in the field of seawater desalination.
海水反渗透淡化技术（SWRO）具有工程投资低、建造周期短、占地面积小、运行维护简便、能耗低、制水成本低等优势。尤其是采用了更高效的能量回收装置、提高水回收率等措施后，大大降低单位产水的能耗，海水淡化吨水能耗将由目前的4.0～5.5kwh/m3下降到2.5～4.5 kwh/m3。经过近几年的发展，反渗透海水淡化工程技术越来越成熟，成套设备制造能力越来越强，应用规模越来越大，海水反渗透海水淡化技术已逐渐成为海水淡化的主流技术之一。
According to the raw seawater data, product water data of the project and application of brine, we recommend thermo and membrane hybrid technique: NF-RO-MED/TVC. The process flow sheet and water balance referred to figue7.1~7.2. The advantages of the process are showed as follows: it can be sharing the seawater intake; can be fully used low grade steam from the electric plant; the product water can satisfy the vary requirement as the certain proportion, so the cost of seawater desalination is reduced as well as the quantity of brine discharge. Nowadays, the largest of seawater desalination in the world, which is used thermo-membrane hybrid technique, its scale can be reached 454000m3/d, MSF water yield is 284000m3/d, RO water yield is 170000 m3/d
根据本工程进水、产品水以及浓水的用途，推荐采用热膜杂化工艺NF-RO-MED/TVC（纳滤-反渗透-多级蒸馏），工艺流程和水量平衡简图详见图7.1~图7.2。该工艺具有以下优点：可以共用海水取水口，能够充分利用电厂低品位蒸汽，淡化产品水可以按一定比例混合满足不同需求需求，降低海水淡化成本，减少浓水排放量等。目前，世界上最大的热膜联产海水淡化厂已达454000m3/d，其中，MSF产水284000m3/d万立方米，RO产水170000 m3/d。
[image: image1.wmf]Pretreatment

预处理

NF

纳滤

RO

反渗透

MED

多效蒸发

Raw 

Seawater

原海水

800000

m

3

/

d

720000

m

3

/

d

Desalinated 

water

260000

m

3

/

d

460000

m

3

/

d

淡水

Discharged

water

80000

m

3

/

d

Discharged

water

260000

m

3

/

d

200000

m

3

/

d

Desalinated 

water

100000

m

3

/

d

淡水

100000

m

3

/

d

Fig 7.1 Process Flow sheet

[image: image2.wmf]High

-

Density

 

Sedimentation Tank

高密度沉淀池

Filter

过滤

Water tank

水箱

cartridge filter

保安过滤器

NF 

high lift pump

NF

高压泵

NF 

capsule stack

NF 

膜组

Water tank

水箱

Lift pump

升压泵

High lift pump 

& 

energy recovery

高压泵及能量回收

cartridge filter

保安过滤器

        RO

RO

Raw Seawater

RO 

product 

water

Ten

-

effect MED device

Steam

十效

 MED 

装置

M

E

D

 

P

r

o

d

u

c

t

 

W

a

t

e

r

B

r

i

n

e

M

E

D

 

产

水

浓

盐

水

图7.1 工艺流程图

Fig 7.2 Water Balance Flow Sheet
图7.2水量平衡图

The whole seawater treatment flow is included several parts as follows:

整个处理流程可以分为以下几个部分：
7.1 Seawater Intake System 海水取水系统
We propose the mode of water intake adopt the artesian nullah. In order to avoid the influence of debris and biological in seawater, bar screen of 50mm and rotating mesh strainer of 4 × 4mm are set in the nullah. The water pumping station needs to design with 800000 m3/d.

建议采用自流明渠引水的取水方式，为避免海水中杂物及生物的影响，在明渠内设置的50mm间隙粗格栅，4×4mm旋转筛网滤网。取水泵站采用按照80万m3/d设计。
The inlet of priming nullah is more than 0.5cm lower than the guaranteed low tide level of the project needed, and setup the washing cycle according to the actual water quality.

引水渠入口低于工程所要求的保证率低潮位以下大于0.5，并根据取水水质实际情况设定清洗周期。

[image: image3.emf]UF

系统

反洗水排放

臭氧发生器

储水罐 反应罐

尾气分解

桶装水灌装线

桶装水供用户

UF

系统

反洗水排放

臭氧发生器

储水罐 反应罐

尾气分解

桶装水灌装线

桶装水供用户

[image: image4.emf]
Fig 7.3 Coarse Screen           Fig 7.3 Intake water pump station Screen

图7.3粗格栅示意图                  图7.4进水泵站示意图
7.2 Pretreatment System 预处理系统
Pretreatment is of the utmost importance for the seawater desalination, especially for the RO membrane. The RO membrane is more sensitive to the colloid, organism, microorganism, siliceous compound and other pollution in seawater; blockage, scaling and degradation may be caused by the pollutants, ultimately lead to the decline of seawater desalination rate and water production. Therefore, the seawater reverse osmosis desalination system has a special strict requirement on the pretreatment; the pretreatment is an important guarantee for the successful operation of the system.
预处理对于海水淡化工程至关重要，尤其是反渗透膜对进水更加敏感，容易被水中的胶体、有机物、微生物、硅等物质污染，造成反渗透膜的污堵、结垢和膜降解，最终导致系统除盐率和产水量的下降。因此，反渗透海水淡化系统对海水预处理有着特殊严格的要求，预处理是反渗透系统成功运行的重要保证。
For the specific circumstances of this project, coagulative precipitation and multi-medium filter are recommend as the pretreatment. The main function is to remove the suspended solids, colloid, organism, germ, algae, halobios in the raw water.

针对该项目的具体情况，推荐采用混凝沉淀及多介质滤池作为预处理手段。主要作用是去除原水中含有的悬浮物、胶体有机污染物质、细菌、藻类、海生物等。
7.2.1 Unit of Coagulative Precipitation混凝沉淀单元
Coagulation and flocculation sedimentation tank is a pretreatment facilities which take charge of reaction, oxidation, inclined plate clarification and automatic sludge discharge. The filtration rate up to 20m/ h ~ 30m/ h, which enable to reduce the floor space greatly, also makes setting roof on the top of the structure possible, in order to avoid the breeding of algae. The medicine generally adopt inorganic iron salts, aluminum salts, oxidizer, disinfectants and coagulant aid. When water quality break, oxidizer and powder activated carbon can be dosed as an emergency measure.
混凝沉淀池是集絮凝反应、氧化、斜板澄清、自动排泥于一体的预处理设备，滤速可达20m/h~30m/h，占地面积大大减小，这也使得池体顶部设置顶棚成为可能，从而避免藻类滋生。药剂一般可投加无机铁盐、铝盐、氧化剂、消毒剂、助凝剂等。水质突变时可以投加氧化剂和粉末活性炭作为应急措施。
[image: image5.emf]
Fig7.5 coagulative precipitation tank
图7.5 混凝沉淀池示意图

7.2.2 Multimedia filtration unit多介质过滤单元
Multimedia filter can make use of one or several media to remove suspended impurities, microorganisms and colloids from water. The filter commonly used are quartz sand, anthracite coal and manganese grain, which can be used in turbidity removal, water softening, and pretreatment of purified water, etc. 

多介质过滤器是利用一种或几种过滤介质，有效去除水中的悬浮杂质、微生物和胶体物质，使水澄清的过程。常用的滤料有石英沙，无烟煤，锰砂等，主要用于水处理除浊，软化水，纯水的前级预处理等。过滤速度一般小于8m/h，一般每天自动反冲洗一次。

The quality of effluent treated by pretreatment system is as follows: turbidity ≤ 1NTU, CODMn≤ 3 ppm, and SDI≤5, which protects the following equipment run firmly.

预处理系统出水水质可以达到：浊度≤1 NTU；CODMn≤ 3 ppm， SDI≤5，从而更有效地保护后续设备的稳定运行。

[image: image6.png]



Fig.7.6 Multimedia filter in a seawater desalination plant

图7.6 某海水淡化厂多介质过滤装置
7.3 Nano filter System纳滤系统

According to our engineering experiment, organic pollutants(TOC) in seawater is composed mainly of small molecules. More than 80% of molecular weight of TOC is less than 1000, while NF can get rid of molecular weight between 200 and 1000. Therefore, NF is the most suitable process for organic-removing.

根据我方工程经验，一般海水有机污染物质（TOC）中以小分子为主，一般海水中80%以上的TOC物质分子量小于1000，而纳滤截留分子量一般恰好在200~1000之间，因此，对于有机物质的去除最适合的处理工艺就是纳滤。
NF is also effective in the removal of inorganic substances. The retention rate of sodium chloride is 40%~90%, and that of ions especially anions is up to 99%. As a result, the osmosis pressure of effluent is reduced and the recovery rate of the following RO system and MED system is improved.

同时，纳滤对氯化钠截留率一般40~90%，对二价离子特别是阴离子截留率可达99%，可以有效降低出水渗透压，提高后续反渗透及MED系统的回收率。

The NF system consists of the high-pressure pump, NF membrane module, cleaning system, dosing system, etc.

纳滤系统包括高压泵、纳滤膜组件、清洗系统、加药系统等。

In this design report, we adopt NF27-2400 NF membrane, which is used one stage-two phase design, totally used 10556 pieces of NF membrane modules. Additionally, the device also includes dosing system, to remove remaining residual chlorine; adding antisludging agent to protect NF membrane elements and RO membrane elements. Meanwhile, the Stiff & Davis index of raw water will improved from 0 to 1.5, to prevent scale formation and dangerous for membrane.
本次设计纳滤采用NF27-400纳滤膜，采用一级两段设计，共使用NF膜10556支，此外还设加药系统去除余氯、添加阻垢剂，以防止破坏纳滤膜元件及后续的反渗透膜元件，同时将原水的Stiff & Davis指数由0提高到1.5，防止钙镁硬度在膜内结垢以及硫酸钙等物质对膜的危害。
The product water quality of NF system as follows:

NF系统产水水质如下： 

	Items项目
	Unit单位
	Value值

	pH
	-
	8.0

	TDS
	mg/L
	23537.79

	Cl-
	mg/L
	14626.06

	SO4
	mg/L
	10.71

	Na+
	mg/L
	7254.85

	K+
	mg/L
	451.00

	Ca2+
	mg/L
	390.72

	Mg2+
	mg/L
	804.42


The reject water quality of NF system as follows：
NF系统排放浓水水质如下： 

	Items项目
	Unit单位
	Value值

	pH
	-
	8.0

	TDS
	mg/L
	67029.22

	Cl-
	mg/L
	41168.75

	SO4
	mg/L
	1180.11

	Na+
	mg/L
	19183.85

	K+
	mg/L
	1233.86

	Ca2+
	mg/L
	954.38

	Mg2+
	mg/L
	3308.93


7.4 RO System 反渗透系统

SWRO system is included of lift pressure pump, RO membrane module, energy recovery equipment, flushing system and cleaning system etc.

反渗透海水淡化系统（SWRO）由：高压泵、反渗透膜组件、能量回收装置、冲洗系统、清洗系统等组成。

RO system is one of the key devices in seawater desalination system, which can remove soluble salts, colloids, organics and microorganism. According to the water quality, one stage RO membrane applies compound RO membrane, which is especially suitable for the seawater, each piece of membrane can reach a 99.6% desalination rate, and the length of each membrane is 1m.

其中，反渗透是整个海水淡化系统脱盐的关键设备之一。它负责脱除水中的可溶性盐分、胶体、有机物及微生物，使出水水质达到用户的要求。根据水质情况，一级反渗透膜采用了适合海水淡化的复合反渗透膜，单根脱盐率可以达到99.6%，膜的长度为1米。
[image: image7.jpg]


Fig 7.7 SWRO membrane modules

图7.7 SWRO膜元件

Considering the pressure of the discharged condensed water is more than 5 MPa, to recover more brine energy, reduce more consumption, in our design report, we set energy recycle Instrument (ERI), the recycle rate of ERI is above 90%, which will decrease 30% consumption.
由于排放的浓盐水压力超过5MPa，为了有效回收浓盐水的能量，降低系统能耗，本次设计设置了能量回收装置（ERI），能量回收装置的能量回收效率在90%以上，可降低30%能耗。

The principle of ERI is shown as follows: the raw water inter to the RO device, is divided into two parts, one is 40% of the water passes through the high pressure pump, to lift pressure, and meet the requirement of the RO operation. The other one is 60% of the water passes the PX device to make the energy exchange, which make the water pressure increased close to RO operation pressure. The insufficient pressure is compensated by the booster pump.

它的工作原理是进入反渗透装置的原水分成2 路，一路是40%的水量通过高压泵增压至反渗透的运行压力，另外一路60%的水量通过PX装置进行能量交换，使给水的压力增加接近反渗透的运行压力，不足部分由增压泵升压补偿达到与高压泵出口相同的压力。
[image: image8.wmf]Pretreatment

预处理

NF

纳滤

RO

反渗透

MED

多效蒸发

Raw 

Seawater

原海水

800000

m

3

/

d

720000

m

3

/

d

Desalinated 

water

260000

m

3

/

d

460000

m

3

/

d

淡水

Discharged

water

80000

m

3

/

d

Discharged

water

260000

m

3

/

d

200000

m

3

/

d

Desalinated 

water

100000

m

3

/

d

淡水

100000

m

3

/

d


Fig 7.8 SWRO ERI
图7.8 SWRO能量回收装置
The product water quality of RO system as follows:

RO系统产水水质如下： 

	Items项目
	Unit单位
	Value值

	pH
	-
	8.0

	TDS
	mg/L
	75.50

	Cl-
	mg/L
	45.92

	SO4
	mg/L
	0.00

	Na+
	mg/L
	26.22

	K+
	mg/L
	1.83

	Ca2+
	mg/L
	0.48

	Mg2+
	mg/L
	1.02


The brine quality of RO system as follows 
RO系统排放浓水水质如下： 

	Items项目
	Unit单位
	Value值

	pH
	-
	8.0

	TDS
	mg/L
	42734.21

	Cl-
	mg/L
	26555.27

	SO4
	mg/L
	19.47

	Na+
	mg/L
	13169.18

	K+
	mg/L
	818.50

	Ca2+
	mg/L
	710.01

	Mg2+
	mg/L
	1461.75


7.5 多效蒸馏系统（MED）Multiple Effect Distillation System (MED)

4 MED units, each of 25000m3/d capacity are adopted system. Each unit is equipped with 10 effect system, and the last distillation equipment shall be connected with condensator.
多效蒸馏系统（MED）采用4台单机产水容量为25000m3/d的MED装置，每台装置采用10效系统，最后一效蒸发器同冷凝器相连。
Raw water will first enter into the columns with lowest temperature in the distillator and be preheated, then be sprayed to the top pipes of each distillator. Part of sea water will absorb heat and boil off when flow down. The thickened water will enter into the next column, and repeat spraying and evaporation. At last, the remains will be separated in the last column with lowest temperature as thickened water.

进料水进入蒸发器最低温度组中，经液体分布器喷淋到各蒸发器的顶排管上，在自上而下以薄膜形式流动的过程中，部分海水因吸热而汽化，被浓缩的料液进入蒸发器效的下一组中，在新的效组中重复蒸发和喷淋过程。剩余的料液往前打，并在温度最低的效组中以浓缩液的形式离开。
The steam used to heat sea water shall first enter into the 1st effect evaporating pipes with highest temperature, and condensate. Steam made from sea water will enter into the 2nd effect evaporating pipes. The evaporation-condensation process will be repeated, almost equal amount of distillated water will be produced in each effect column, and steam produced in last effect column shall be condensated by cooling water. 

加热用的蒸汽输入到温度最高一效的蒸发管内部，并在管内冷凝。产生的二次蒸汽经过汽液分离器后，进入下一效的传热管。这种蒸发冷凝过程逐效重复，每效产生几乎同等数量的蒸馏水，最后一效的蒸汽在冷凝器中被冷却水冷凝。
Distilled water produced in the 1st effect column will return to the boiler to compensate water evaporated, water produced in later columns will be cooled and pumped into the product tank.

第一效产生的蒸馏水返回锅炉，以补偿提供蒸汽消耗的淡水，第二效以后的蒸馏水经过逐效闪蒸冷却，在最后一效用产品水泵抽出并输入到产品水罐中。浓缩盐水也象蒸馏水一样，经过逐效闪蒸以提高系统的热效率。最后产生的浓盐水进行排放或制盐。

[image: image9.wmf]High

-

Density

 

Sedimentation Tank

高密度沉淀池

Filter

过滤

Water tank

水箱

cartridge filter

保安过滤器

NF 

high lift pump

NF

高压泵

NF 

capsule stack

NF 

膜组

Water tank

水箱

Lift pump

升压泵

High lift pump 

& 

energy recovery

高压泵及能量回收

cartridge filter

保安过滤器

        RO

RO

Raw Seawater

RO 

product 

water

Ten

-

effect MED device

Steam

十效

 MED 

装置

M

E

D

 

P

r

o

d

u

c

t

 

W

a

t

e

r

B

r

i

n

e

M

E

D

 

产

水

浓

盐

水


Fig 7.8 MED device
图7.8 MED装置
Diagram 7.9 are phase map of calcium sulphate change with temperature. The blue is operating specification of low temperature multiple effect distillation system. Calcium sulphate is hard to be removed if scale, for it can’t be dissolved by acid or alkali, and integrated with the heat interchanger hardly. Therefore, the weight concentration normally shall be 2 in low temperature MED, and the operating temperature shall not be higher than 70℃ to avoid scaling. 

图7.9是硫酸钙随温度变化的相图，蓝色区域是低温多效蒸馏的操作范围。与碳酸钙相比，硫酸钙结垢以后很难去除，因为它不能溶于酸也不能溶于碱，而且与换热器的结合程度非常牢固。因此，采用低温多效蒸馏时海水的浓缩倍数一般为2，操作温度一般不高于70℃，就有效地避免无机盐的结垢。
As is said before, the concentration of calcium ion magnesian ion of NF thickened water are close to that of MED, therefore, MED is not fit for NF thickened water treatment. 

如前所述，本项目NF浓水钙、镁离子浓度与MED浓水接近，因此不适合再进行多效蒸馏。

[image: image10.png]G ——— =

R — I
7z - 7 ¢ 7 WTITITEIE S S S S8 S S
E & = L=




Fig 7.9 low temperature multiple effect distillation principle
图7.9低温多效蒸发的操作原理
The salt content of the product water from low temperature multiple effect distillation device is generally less than 10mg/L, the water quality of MED product water shows as follows:

低温多效蒸馏装置产品水的含盐量一般小于10mg/L，MED产水水质水质如下： 

	项目Items
	单位Unit
	值Value

	pH 
	-
	8.0

	TDS
	mg/L
	＜10

	Cl-
	mg/L
	＜5

	SO4
	mg/L
	＜1

	Na+
	mg/L
	＜5

	K+
	mg/L
	＜1

	Ca2+
	mg/L
	＜1

	Mg2+
	mg/L
	＜1


The brine quality of low temperature multiple effect distillation devices as follows:

低温多效装置排放的浓水水质如下：
	Items项目
	Unit单位
	Value值

	pH
	-
	~7

	TDS
	mg/L
	85468.42 

	Cl-
	mg/L
	53110.53 

	SO4
	mg/L
	38.95 

	Na+
	mg/L
	26338.37 

	K+
	mg/L
	1637.01 

	Ca2+
	mg/L
	1420.01 

	Mg2+
	mg/L
	2923.49 


7.6 Bottled water system 瓶装水系统 
Two kinds of Bottling Line, bottled pure water and barreled pure water are adopted. There shall be 9 bottling lines with capacity of 2L, which can produce 250ml,288,000 bottles of water per day, or 500ml,144000 bottles of water per day, or 1.5L, 45000 bottles of water per day; 3 Bottling lines with capacity of 1 gallon and 3 Bottling lines with capacity of 5L, which can produce 1 gallon,54000 bottles of water per day, or 5L, 48000 bottles of water per day; 2 Bottling lines with capacity of 6 gallons, which can produce 36000 bottles of water per day.

瓶装水系统采用瓶装纯净水灌装线和桶装纯净水灌装线两种。其中2 L的灌装线9条，产量可达250 mL的28.8万瓶/天，500 mL的14.4万瓶/天，1.5 L的4.5万瓶/天；1加仑和5 L的灌装线各三条3条，产量可达1加仑的5.4万瓶/天，5 L的4.8万瓶/天；6 加仑的2条，产量可达3.6万瓶/天。
Bottling lines are made up of lid pulling, barrel clean, bottle arrangement, bottling, lid clean, light check, Hot charge membrane, and product transform system, all of them are totally automatic. Machine body  is made of stainless steel,  transform belt is made of ABS engineering plastics, and the process lines are totally automatically controlled by PLC, and close operation is adopted to ensure no secondary pollution happens. The bottling workshop covers 3220m2.

灌装线包括全自动拔盖机系统、自动刷桶机系统、自动上瓶机系统、全自动灌装系统、自动洗盖和送盖系统、灯检系统、自动热收膜系统和成品输送系统。机身主要采用优质不锈钢制作，输水带采用ABS工程塑料输送带，整个生产线采用PLC控制，生产过程采用封闭式运行，保证整个洗瓶、灌装过程不会发生二次污染。瓶装水车间总占地3220m2。

[image: image11.jpg]



The whole bottled water process should have ozone sterilize and ultra Filter.
制水工艺采用臭氧消毒、超滤。
8. Estimated Cost 工程估算

The total cost of the whole project is estimated 75752.724 million USD.

Notes:

1. Due to the lack of the information of geology, the investment of the intake water proposal maybe adjusts. 

2. Due to the lack of detailed site information, the investment of construction maybe adjusts.

3. The length of intake seawater pipe line is an estimated value, it should be adjusted according to the factual situation. 
说明：
1.由于缺少项目取水地勘察资料，取水部分方案及投资可能会有所调整。

2.由于没有厂址详细设计资料，土建投资可能会有所调整。

3.海水输水管道长度为估计值，应根据实际情况调整。
9. Equipment List and Specifications主要设备清单及设备说明
	Items 
项目
	Specifications 
规格参数
	number 数量
	Notes 
备注

	01.粗格栅 Coarse Screen

	1 set of 3 cells 一池3格

	抓斗式粗格栅
grab type coarse screen
	B=4m b=50mm H=4.5m a=30℃
	3
	　

	电动闸门 
electric gate valve
	DN1800
	4
	　

	02.细格栅及提升泵房 Fine Screen & Lift Pump

	1 set

	旋转滤网细格栅 
rotary sieve fine screen
	B=2.5m b=4x4mm
	4
	　

	离心泵 
centrifugal pump
	Q=5417m3/h H=10m P=225kw
	10
	8用2备

	03 高密度沉淀池 High-Effective Sedimentation Tank

	2 sets of 8 cells

	电动进水闸板阀
electric slide valve
	WxH=1.20x1.20m  N=2.2kW
	8
	　

	混凝池快速搅拌器 
flash mixer
	D=1.6m 轴长L=5.06m  N=5.5kW
	8
	　

	投加池快速搅拌器 
flash mixer
	D=1.6m 轴长L=5.06m  N=5.5kW
	8
	　

	熟化池慢速搅拌器 
slow stirrer
	D=2.4m 轴长L=4.06m  N=11kW
	8
	　

	斜管 
pipe chute
	L=1.04m  d=40mm
	592
	　

	刮泥机 
mud scraper
	D=10.8m N=2.2kw
	8
	　

	电动出水闸板阀 
electric slide valve
	WxH=1.8x1.8m  N=2.2kW
	2
	　

	微砂循环泵 
recycle pump
	Q=150m3/h  H=17m  N=15kW
	24
	16用8备

	微砂投加系统 
dosing system
	N=1.5kw
	2
	　

	空气压缩机系统 
air compressor systems
	Q=240Nm3/h,P=6bar,N=30kW
	　
	　

	高分子制备单元 
polymer made unit
	Capacity=6.0m3/h  N=2.2kW
	　
	　

	螺杆泵 
PC pump
	Q=8.5~11m3/h, H=20m,N=1.5kW
	12
	10用2备

	04. 滤池 Filter Chamber

	4 Sets

	反冲洗鼓风机 
back flush Blower
	Q＝2400m3/h P＝3.92m N＝50kW
	3
	2用1备

	反冲洗离心泵 
back wash centrifugal pump
	Q=720m3/h H=10m P=30kw
	3
	2用1备

	气动模拟调节蝶阀 Pneumatic Butterfly Valve
	DN400
	48
	　

	气动蝶阀  
Pneumatic Butterfly Valve
	DN600
	48
	　

	气动蝶阀 
 Pneumatic Butterfly Valve
	DN450
	48
	　

	手动蝶阀  
Butterfly Valve
	DN400
	48
	　

	手动蝶阀 
Butterfly Valve
	DN450
	8
	　

	电磁阀 
solenoid pilot actuated valve
	DN50
	48
	　

	手动闸板 
flashboard
	600×600
	48
	　

	气囊阀 
gasbag valve
	　
	48
	　

	气动闸板 
airioerating flashboard
	700×700
	48
	　

	堰板 
cut-off wall
	500×2000
	48
	　

	手动蝶阀 
Butterfly Valve
	DN150
	48
	　

	滤板 
filter board
	980×980
	4608
	　

	滤头 
filter
	　
	258048
	　

	05. NF&RO 膜车间 NF & RO Membrane Workshop

	2 sets

	原料水泵 
raw water pump
	Q=2580m3/h H=10m 
	13
	　

	次氯酸钠消毒系统 
NaClO disinfect system
	30 kg/h 1.5mg/L
	1
	　

	絮凝剂加药系统 flocculent dosing system
	 30 kg/h 5mg/L
	1
	　

	NF升压泵 
NF booster pump
	Q=1260m3/h H=20m 
	26
	　

	加NaHSO3系统 
NaHSO3 dosing system
	　
	26
	　

	阻垢剂加药系统 antisludging agent dosing system
	　
	26
	　

	NF高压泵 
NF booster pump
	Q=760m3/h H=322m 
	26
	　

	 NF能量回收装置 
energy recycle device
	　
	26
	　

	 NF增压泵 
pressure pump
	Q=510m3/h H=40m 
	26
	　

	 NF膜组（一级两段）capsulestack
	10000 m3/d DOW NF270-400 单组812个
	26
	　

	NF清洗系统
 scavenger system
	　
	13
	　

	 NF产水水箱
 product water tank
	　
	13
	　

	反渗透取水水泵 RO intake water pump
	Q=758m3/h H=30m 
	26
	　

	保安过滤器 
cartridge filter
	Q=758m3/h H=10m 
	26
	　

	 高压泵 
high lift pump
	Q=416m3/h H=649m 
	26
	　

	 能量回收装置
energy recycle device
	PX-260 50~59 m3/h
	26
	　

	增压泵 
booster pump
	Q=392m3/h H=40m 
	26
	　

	反渗透膜堆 
RO membrane stack
	　
	26
	　

	 反渗透清洗系统 RO scavenger system
	出力 10000 m3/d 回收率 55%
	13
	　

	06.MED system

	4 sets

	MED系统 
MED Device
	2.5万吨/日
	4
	　

	MED海水进料泵 
intake seawater pump
	Q=2243m3/h H=25m 
	3
	2用1备

	MED1-2效进料泵 
1-2 effect feed pump
	Q=1277m3/h H=20m
	2
	1用1备

	MED3-4效进料泵
 3-4 effect feed pump
	Q=1490m3/h H=20m
	2
	1用1备

	MED5-7效进料泵 
5-7 effect feed pump
	Q=1788m3/h H=20m
	2
	1用1备

	MED8-10效进料泵 
8-10 effect feed pump
	Q=2083m3/h H=20m
	2
	1用1备

	冷却水排放泵 
waste water pump
	Q=1201m3/h H=15m
	3
	2用1备

	浓盐水排放泵
 brine pump
	Q=1042m3/h H=15m
	2
	1用1备

	冷凝水返回泵 
condensed water pump
	Q=127m3/h H=30m
	2
	1用1备

	淡水泵 
product water pump
	Q=1042m3/h H=30m
	2
	1用1备

	酸洗泵 
acid washing pump
	Q=694m3/h H=30m
	1
	　

	阻垢剂计量泵 
antisludging agent metering pump
	50 kg/h 4.2bar
	1
	　

	07.清水池 Clean Water Pond 

	2 sets

	08.送水泵房 Transmission Pump Station 

	1 set

	单级双吸卧式离心泵 single-stage double suction centrifugal pump
	Q＝2500m3/h H＝15m N＝250kW
	12
	8用4备

	潜水排污泵 
sewage submersible pump
	Q＝10m3/h H＝10m N＝0.75kW
	1
	　

	09.瓶装水制备车间 Bottled Water Workshop

	1 set

	250 mL生产线 
production line
	 28.8万瓶/天
	3
	　

	500 mL生产线 
production line
	14.4万瓶/天
	3
	　

	1.5 L生产线 
production line
	 4.5万瓶/天
	3
	　

	1加仑生产线 
production line
	5.4万瓶/天
	3
	　

	5L生产线 
production line
	4.8万瓶/天
	3
	　

	6加仑生产线  
production line
	3.6万桶/天
	2
	　

	车间消毒系统 
 disinfectant device
	　
	1
	　

	10.污泥浓缩池 Sludge Concentration Tank

	Φ16m 2 sets

	中心传动浓缩机
 centre drive densifier
	D=16m
	2
	　

	11.脱水机房 Dewatering House

	1 set

	离心脱水机
centrifugal drier
	Q=20~30m3/h,N=11kW
	2
	1用1备

	进泥泵 
PC pump
	Q=12~60m3/h,H=20m,N=18.5kW
	2
	2用1备

	絮凝剂制备装置
 PAC made device
	　
	1
	　

	加药泵 
chemical dosing pump
	　
	2
	1用1备

	稀释盘 
dilute plate
	　
	2
	1用1备

	无轴螺旋输送机（水平）
horizontal screw conveyer
	Q=4~8m3/h,L≈8m,N=5.5kW
	1
	　

	无轴螺旋输送机（倾斜）lean screw conveyer
	Q=4~8m3/h,L≈11m,N=7.5kW
	1
	　


10.附件Attachment
10.1. Preliminary of the process flow sheet 初步工艺流程图
Please see the attachment 1~4.
10.2. Layout of the process 工艺平面布置图
Please see the attachment 1~4.
� EMBED Visio.Drawing.11  ���











� EMBED Visio.Drawing.11  ���








26

[image: image12.png]17.5

14
105

35

€aS04.2H:0

CasSO,

€Cas$04.12H20




[image: image13.png]


_1321871342.vsd
�

Pretreatment
预处理�

NF
纳滤�

RO
反渗透�

MED
多效蒸发�

Raw Seawater


原海水


800000m3/d


Desalinated water


720000m3/d


260000m3/d


460000m3/d


淡水


Discharged
water


80000m3/d


Discharged
water


260000m3/d


200000m3/d


Desalinated water


100000m3/d


淡水


100000m3/d



_1321874068.vsd
�

�

�

�

�

�

�

�


