MAN 10L32/44DF Generator sets

For Nigeria Dual Fuel Power Plant Project

# 2023 07 28

# Overview

Main technical parameters of the Dual Fuel generator set are as follows:

- Output power of generation: 5.4MW 11KV 50Hz

- Model of the generator set: MAN10L3244 DF generator set

- Number of generator sets: 3 sets

- Output voltage of the unit: 11KV

- Frequency: 50Hz

- Cooling method:  Pressure water circulating air cooling by airing.

- Fuel：LNG and HFO/LFO；

In order to keep the output power of the engine under full load without any discount or reduction, the natural gas quality shall meet the following specifications:

| Characteristic parameter | Unit | Value |
| --- | --- | --- |
| Lower heating value （LHV） min. | MJ/m3N) | 24 |
| Methane number （MN） min. | --- | 80 |
| Methane （CH4） min. | Volume ratio % | 70 |
| Hydrogen（H2S） max. | Volume ratio % | 0.05 |
| Hydrogen （H2） max.2 | Volume ratio % | 3 |
| Ammonia max. | mg/m3N | 25 |
| Chlorine, fluorine，max. | mg/m3N | 50 |
| Particles and solids (engine inlet), max. | mg/m3N | 50 |
| Particles and solids (engine inlet), max. size | um | 5 |
| Gas inlet temperature | ℃ | 5～50 |
| Liquid water and hydrocarbons are not allowed at engine inlet |  |  |

DO/HFO with pretreatment; the basic requirements are as follows: viscosity at the engine inlet port 2.0-12 mm2/s (cSt)

| Characteristic parameter | Unit | Value |
| --- | --- | --- |
| Viscosity at 40°C | cSt | 2.0～12.0 |
| Density at 15°C max. | kg/m3 | 890 |
| Sulphur max. | Quality % | 1.5 |
| Flash point min. | ℃ | 60 |
| Sediment max. | Quality % | 0.1 |
| Pour point (upper), Winter max. | ℃ | -6 |
| Pour point (upper), Summer max. | ℃ | 0 |
| Water | Volume % | ≤0.01 |
| Ash | Quality % | ≤0.01 |

* HFO has a high sulfur content, which will cause accelerated wear of important parts of the engine, and at the same time, the emission of sulfur compounds exceeds the standard.

Notices for operation on Natural Gas:

—Switching load of gas mode is 30%～70% in generator output

—Natural gas pressure must be kept stable between 6.5 to 8.5 bar (before GVU, pressure volatility

≤±4%/s)

## Main technical Specifications and Parameters

Table 1	Technical parameters of engine (under standard conditions)

| Item | Unit | Value |
| --- | --- | --- |
| Model of engine |  | MAN10L3244DF |
| Rated power of engine | kW | 5400 |
| gas heat rate and fuel consumption | MJ/kwh /g/kwhr | 9/188+5% |
| Number of cylinder | Pcs. | 10 |
| Cylinder diameter | mm | 320 |
| Stroke | mm | 440 |
| Discharge capacity | L | 366 |
| Rotating speed | rpm | 750 |
| Mean velocity of piston | m/s | 10.5 |
| Filling capacity of lubricating oil | m3(kg) | 2.2(1826) |
| Water filling capacity | m3(kg) | 1.5(1500) |
| Length ×Width×Height | mm | 8800* 1900 *4536 |
| Net weight | kg | 65000 |

Table 2 Technical data sheet of electric generator (under standard conditions)

| Model | Unit | TFC/ZFC |
| --- | --- | --- |
| Rated power | kW | 4600 |
| Power factor | COSφ | 0.8 |
| Frequency | Hz | 50 |
| Voltage | kV | 6.6 |
| Rotating speed | rpm | 750 |
| Allowed overspeed | rpm | 120% |
| Efficiency | % | 96 |
| Moment of inertia (flywheel) | kgm2 | 590 |
| Weight | kg | 16500 |
| Anti-radio jamming grade |  | N |
| Structure type |  | IBM3 |
| Insulation class |  | F/B |
| Protection class |  | IP23 |
| Allowable temperature rise under rater power | 0C | 80 |
| Maximum surrounding ambient temperature | 0C | 40 |
| Total harmonic distortion | % | 3% |
| Reactance and time constant |  |  |
| xd direct-axis synchronous reactance | % | 195.6% |
| xd¹ direct-axis transient reactance | % | 24.4% |
| xd” direct-axis subtransient reactance | % | 16% |
| Time constant of Td” subtransient reactance | sec | 0.018 |
| Td time constant | sec | 4.187 |

Table 3 Summary sheet of main technical parameters for generator set(under standard conditions)

| Model |  | 4600DF |
| --- | --- | --- |
| Rated power of generator set | kW | 4600 |
| Power factor |  | 0.8 |
| Rotating speed | rpm | 750 |
| Heat value of fuel gas | MJ/NM3 | 40-45 |
| Intake pressure of fuel gas | kPa | 510~980 |
| Exhaust gas temperature | 0C | 540 |
| Allowable exhaust back pressure | kPa | 4.5 |
| Exhaust gas emission | Nm3/h | 24700 |
| Minimum heat value applicable to gas | MJ/Nm3 | 32 |
| Fuel consumption | MJ/kWh/g/kwh | 9/192+5% |
| Lubricating oil consumption | g/kWh | 0.4-0.6 |
| Generating efficiency | % | 44 |
| Heat efficiency | % | 28.2 |
| Overall efficiency | % | 72.2 |
| Cylinder diameter/stroke | mm/mm | 320/440 |
| Backwater/effluent temperature of cylinder liner water | 0C/0C | 74/82.5 |
| Water volume of cylinder liner | m3/h | 82 |
| Output voltage | kV | 6.6 |
| Frequency | Hz | 50 |
| Net weight of engine unit | T | 91 |
| External dimension of engine unit | m | 11.565x2.235x4.78 (length x width x height) |

# 3.   Main generator set

### The main generator set is composed of dual fuel engine, main generator and common under frame and ancillary facilities (electric barring device, oil mist detector, etc.) The side cabinet and instrument cabinet installed at the side of the set are able to display and monitor the working condition and alarm instruction of the engine as well as give orders to engine for real-time control. The startup preparation, start, synchronized grid connection, load control, shutdown and emergency shutdown of the set may carry out on the side cabinet of the set.

Engine is the engine with four strokes, L-type arrangement, exhaust turbine pressurization, air inter cooling, the DO ignites and lean combustion. The engine is equipped with Real Time Intelligent Control System (RICS), and when the gas behavior, outside atmospheric conditions and load conditions are changed, the combustion will be automatically stabilized and be controlled under the optimum conditions.

Compressed air is used for the startup of the engine, and the high pressure air enters into the cylinders successively in sequence under the control of the main starting valve to drive the piston motion and achieve the startup of the engine. By using such startup mode, sparkles possibly generated in the DC motor startup can be avoided, which is safer under the service environment of the gas.

The pressure cooling water circulation system of the engine is divided into the primary water circulation (internal circulation of the engine) and secondary water circulation (circulation outside the unit). The cooling water pump of the circulation system is the motor driven gear pump, and the anti freezing fluid will not be used for the cooling medium. See the water quality requirements in the attached material. Primary circulating water is in closed circulation in the engine interior, mainly for the cooling of high-temperature components, such as cylinder liner of the engine, pressurizer, etc. Air inter-cooler is divided into high temperature section and low temperature section, and the high temperature section is cooled by the primary circulating water. Secondary circulating water from the cooling tower will successively flow through the low temperature section of the air inter-cooler, lubricating oil cooler, primary circulating water cooler for the cooling and heat dissipation of supercharged air, lubricating oil and secondary circulating water. The unit circulation system is equipped with several temperature sensing valves to ensure that the water temperature is controlled within the design range. To adapt to the cold climate in winter of the north, primary water circulation system is installed with cooling water heater (arranged in the auxiliary system of the unit) to ensure that the engine can be started up even under lower temperature.

The friction parts of the moving components in the engine are subject to lubrication, anti-friction, cooling and cleaning by the lubricating oil system of the engine. The lubricating oil is pressurized by the gear lubricating oil pump, which is directly driven by the shafting of the engine, and then flows to the oil sites through the internal camber passages and pipelines of the engine. The internal integration of the common underframe of the engine is equipped with lubricating oil tank, which is served as the oil storage tank and oil return tank of the circulation oil of the lubricating oil system of the engine, so as to meet the daily oil demands of the engine.

The functions of filtration, control and metering, etc. of fuel gas are achieved by the fuel gas system of the engine, and the air-fuel ratio control, power and rotation rate control, etc. are completed together with the electronic control system of the engine. Using Do ignition directly. The gas will enter into the engine cylinder by the gas pipes on both sides of the engine through the gas solenoid electric valve, and then enter into the branch pipe and be mixed with the pressurized air from the pressurizer and air cooler, and finally enter into the cylinder for combustion and power stroke.

The air inlet pipe of the engine (in front of the pressurizer) is installed with air cleaner and intake muffler. The exhaust of the pressurizer is connected with the exhaust system of the unit by the expansion bellows, and the exhaust will be subject to follow-up treatment and utilization after entering into the exhaust muffler and waste heat pipes. The exhaust manifold in front of the pressurizer of the engine is also equipped with exhaust explosion proof equipment and its exhaust pipe. The explosion proof exhaust pipe is equipped with exhaust muffler, too.

## The list of standard spare parts

| No. | Designation | Unit | Qty/Plat | Remark |
| --- | --- | --- | --- | --- |
| 1 | Inlet valve cone,plasma-nitrided | pc | 2 |  |
| 2 | Exhaust valve cone,plasma-nitrided | pc | 2 |  |
| 3 | Valve guide | pc | 2 |  |
| 4 | Pressure spring | pc | 2 | 8×51×178 |
| 5 | Pressure spring | pc | 2 | 12×81×193 |
| 6 | Inlet valve seat ring | pc | 2 |  |
| 7 | Outlet valve seat ring | pc | 2 |  |
| 8 | Valve rotating device | set | 2 |  |
| 9 | Axial bearing | set | 2 |  |
| 10 | Valve cone piece two-part | set | 2 |  |
| 11 | Assembly starting valve | set | 1 |  |
| 12 | Set of gaskets | pc | 4 |  |
| No. | Designation | Unit | Qty/Plat | Remark |
| 13 | Round seal ring | pc | 9 |  |
| 14 | Round seal ring | pc | 15 | 72.62×3.53 |
| 15 | Round seal ring | pc | 6 | 94.92×2.62 |
| 16 | Round seal ring | pc | 6 | 59.69×5.33 |
| 17 | Round seal ring | pc | 6 | 23.40×3.53 |
| 18 | Round seal ring | pc | 6 | 405.26×5.33 |
| 19 | Round seal ring | pc | 6 | 18.64×3.53 |
| 20 | Round seal ring | pc | 6 | 354.97×5.33 |
| 21 | Round seal ring | pc | 6 | 37.47×5.33 |
| 22 | Fire land ring | pc | 1 |  |
| 23 | Round seal ring | pc | 6 | 405.26×5.33 |
| 24 | Seal ring H=10 | pc | 1 |  |
| 25 | Upper bearing shell | pc | 1 |  |
| 26 | Lower bearing shell | pc | 1 |  |
| 27 | Stud screw | pc | 2 | M42×3 |
| 28 | Nut | pc | 2 | M42×3 |
| 29 | Stop piece | pc | 2 |  |
| 30 | Hexagon bolt | pc | 2 | M24×280 |
| 31 | Hexagon bolt | pc | 2 | M24×560 |
| 32 | Hexagon nut | pc | 4 | M24 |
| 33 | Cylinder pin | pc | 2 | 12m6×32 |
| 34 | Hexagon bolt | pc | 12 | M24×180 |
| 35 | Hexagon bolt | pc | 4 | M12×80 |
| 36 | Thrust bearing ring | pc | 2 |  |
| 37 | Hexagon bolt | pc | 8 | M20×180 |
| No. | Designation | Unit | Qty/Plat | Remark |
| 38 | Nut | pc | 8 | M48×3 |
| 39 | Gasket | pc | 6 |  |
| 40 | Round seal ring | pc | 6 |  |
| 41 | Round seal ring | pc | 6 |  |
| 42 | Round seal ring | pc | 6 |  |
| 43 | seal ring | pc | 6 |  |
| 44 | Fuel injection pipe covered | set | 1 |  |