Technical Agreement For 150MVA Double Fuel Power Plant

(20240218)

CONTENT

1. GENERAL DESCRIPTION	3

1.1 GENERAL	3

1.2 DESIGN CONDITION AND PERFORMANCE DATA	3

1.3 FUEL OIL FOR ENGINE	4

1.4 LUBRICATING OIL FOR ENGINE	4

1.5 COOLING WATER FOR ENGINE	4

1.6 STANDARDS	6

1.7 UNIT AND LANGUAGE	6

1.8 TEST AND INSPECTION	6

1.9 PAINTING	7

2. CONFIGURE OF POWER PLANT SYSTEM	7

2.1 GENERATING SETS	8

2.2MECHANICAL AUXILIARY SYSTEM	11

2.3 ELECTRICAL AUXILIARY SYSTEM	14

3.SCOPE OF SUPPLY	23

# 1. GENERAL DESCRIPTION

## 1.1 GENERAL

（1）Power station selection

According to user requirements:

Middle East climate conditions,150MVA 11/90KV 50HZ  generator set.

Select

7sets MAN10L32/44 HFO generator sets,   5.7MW*7=39.9MW.

23sets CSSC 8M32/42 double fuel generator sets,  3.5MW*23=80.5MW.

total :    30sets generating sets,39.9MW+80.5MW=120.4MW=150.5MVA.

Taking into account the local climate conditions,85% run :150.5*85%=102.34MW.

30sets generating units are connected to the grid.

Total power: 150.5MVA(120.4MW)

Voltage: 11/90kV(with booster transformer)

Frequency: 50Hz

Power factor: 0.8(lag)

## 1.2 DESIGN CONDITION AND PERFORMANCE DATA

(1) DESIGN AMBIENT CONDITION

Refer to ISO 3046

The standard environmental condition:

| Environmental temperature | 25℃ |
| --- | --- |
| Barometric pressure | 1bar |
| RH (relative humidity) | 30％ |
| Gross Output AT Generator Terminal | 150.5MVA |
| Fuel consumption at Generator Terminal | Oil:190g/kW.h，gas 7.5KJ/KWh,tolerance +5%. |
| Note: Tolerance + 5%, LCV= 42700 kJ/kg, Load 100%, 50 Hz, PF = 0.8 |  |

## Design condition

## Capacity of the genset can be decided under the following design conditions:

## Ambient temperature--------------------------------------------10~45℃

## Fresh water temperature------------------------------------------36℃

## Relative humidity----------------------------------------------------60%

## Atmospheric pressure------------------------------------------101.3kPa(760mmHg)

## Back pressure of turbo-charger---------------------------350mmAq(max 400mmAq)

## Heat exchangers will be designed at fresh water temperature 36℃.

## Under the following limiting ambient conditions:

## Air temp. at turbocharger inlet           40 deg. C

## Water temp. at charge air cooler inlet      30 deg. C

## Deration to power applicable for engine 	0 %( nil)

## Beyond the abovementioned limiting conditions, deration to power as per ISO 3046 will be applicable.

## The engine should be capable of accepting a sudden load as per the guidelines in ISO-8528-5-1993(e). As per this standard, the maximum sudden load increase stages are.

## Baseload %     sudden load   increase to %

## --------------------------------------------------------------------------------

## 1st Stage         0%          40              40%

## 2nd Stage        40%         30	           70%

## 3rd Stage        70%         20	               90%

## 4th Stage        90%         10	              100%

## --------------------------------------------------------------------------------

## During each of the above-mentioned stages of sudden loading, the transient speed drop will be restricted to a maximum value of 10% of the rated speed.

## Otherwise, the number of generator sets should be increased.

## 1.3 FUEL OIL FOR ENGINE

(1) HFO and DO

The viscosity of Diesel oil shall be of≥2 -15cSt at Engine inlet under the power plant operating.

HFO characteristic parameter:

| Characteristic parameter 特性参数 | Unit 单位 | Value 数值 |
| --- | --- | --- |
| Viscosity at 40°C 40℃时粘度 | cSt | 200-380 |
| Density at 15°C 15℃时密度，max. | kg/m3 | 890 |
| Sulphur 含硫量，max. | Quality 质量 % | <1.5 |
| Flash point 闪点，min. | ℃ | 60 |
| Sediment 机械杂质，max. | Quality 质量 % | 0.1 |
| Pour point (upper), Winter 上倾点，冬季，max. | ℃ | -6 |
| Pour point (upper), Summer 上倾点，夏季，max. | ℃ | 0 |
| Water 水分 | Volume 体积 % | ≤0.01 |
| Ash 灰分 | Quality 质量 % | ≤0.01 |

natural gas quality shall meet the following specifications:

| Characteristic parameter 特性参数Unit 单位Value 数值Lower heating value 低热值（LHV），min. 1)MJ/m3N)24Methane number 甲烷数（MN），min.---80Methane 甲烷（CH4），min.Volume ratio体积比 %70Hydrogen硫化氢（H2S），max.Volume ratio体积比 %0.05Hydrogen 氢气（H2），max.2)Volume ratio体积比 %3Ammonia 氨气，max.mg/m3N25Chlorine, fluorine氯、氟，max.mg/m3N50Particles and solids (engine inlet), max.颗粒和固体（发动机进口），max.mg/m3N50Particles and solids (engine inlet), max. size颗粒和固体（发动机进口），最大尺寸um5Gas inlet temperature 燃气进机温度℃5～50Liquid water and hydrocarbons are not allowed at engine inlet 3）发动机进口处不容许有液态的水和烃类3） |  |  |
| --- | --- | --- |

## 1.4 LUBRICATING OIL FOR ENGINE

The Lubricating oil for engine shall be selected from the list of recommended lubricating oil for engine, which shall be of SAE 40.

Lubricating oil specification: CD grade SAE40.(total base value matches sulfur content.)

## 1.5 COOLING WATER FOR ENGINE

The cooling water system is designed for using normal fresh water with corrosion inhibitor, in order to prevent incrustation and corrosion attack.

The following water quality shall be valid:

For Engine (circulation water)

| Property/ feature | Characteristics | Unit | Remark |
| --- | --- | --- | --- |
| Type of water | Distillate or freshwater, free from foreign matter. Not to be used: Sea water, brackish water, river water, brines, industrial waste water and rain water | - | 1) 1°dH (German hardness): 10mg CaO/litre 17.9mg CaCO3/litre 0.357mval/litre 0.179mmol/litre 2) 1 mg/l 1 ppm |
| Total hardness | max. 10 | °dH 1) |  |
| PH-value | 6.5 - 8 | - |  |
| Chloride ion content | max.50 | mg/l 2) |  |

## 1.6 STANDARDS标准

Unless there are specified standards or codes, all design, manufacturing, quality control and tests shall be in accordance with the applicable portions of below listed prominent international and national Standards and Manufacturer's Standards :

- GB    Chinese standards

## 1.7 UNIT AND LANGUAGE

(1) Units

In all correspondences of technical documents, schedules and drawings, metric units of all measurements shall be used.

(2) Language

The english  language shall be used in all documents, drawings, name plates and correspondences between contractor and owner.

## 1.8 TEST AND INSPECTION

(1) Shop test

Diesel engine shall be tested at the shop in accordance with ISO 3046 and manufacturer’s standard.

(2) Site test

Owner shall perform commissioning and start-up with Contractor's technical assistance. Followings shall be checked before or during commissioning;

- Installation check

- Engine & generator coupling and alignment check

- Test to prove correct operation of interlocks, alarm and tripping circuits

- Safety device check

The performance test procedure will be submitted to the Owner.

## 1.9 PAINTING

## All equipment will be painted in accordance with manufacturer's standard and painting color will be informed to the Owner.

# 2. CONFIGURE OF POWER PLANT SYSTEM

Configure of power plant system contains as follows:

| 1 | Generating sets |
| --- | --- |
| 2 | mechanical auxiliary system |
| 3 | electrical auxiliary system |

## 2.1 GENERATING SETS

2.1.1   MAN 10L3244

Gen-set The generating sets mainly include engine, duplex bearing generator, high elasticity shaft coupling and public housing. Diesel and duplex bearing generator are connected by high elasticity shaft coupling, which are also supported and fixed by common bed.

Function of generating sets:

Rated power ---------------------------------------------------------------5700kW

Rated speed ---------------------------------------------------------------750rpm

Rated voltage --------------------------------------------------------------11kV

Rated frequency -----------------------------------------------------------50Hz

PF(Power factor) ----------------------------------------------------------0.8（lagging）

Boundary dimension）---------------------------------------------------约12750×3635×4840（mm）

Dry weight -------------------------------------------------------------------95 t

Steady-state voltage adjusting rate -----------------------------------≤2.5%

Transient voltage adjusting rate ---------------------------------------+20%~-15%

Sudden load changing voltage steady time ------------------------1.5S

Voltage fluctuation rate --------------------------------------------------0.5%

Steady-state frequency adjusting rate -------------------------------≤0.5%

Transient frequency adjusting rate -----------------------------------+10%~-7%

Sudden load changing frequency steady time ---------------------≤5S

Frequency fluctuation rate ----------------------------------------------≤0.5%

Waveform distortion ------------------------------------------------------≤3%

Engine

| Brand and model of engine | MAN 10L3244 |
| --- | --- |
| Pattern | L10, four stroke, direct injection, turbocharger, water cooled, compressed air starting |
| Cylinder bore | 320mm |
| Stroke | 440mm |
| Compressed ratio | 15.2 |
| MCR (Most Continuous Power) | 6000kW |
| Speed | 750r/min |
| Direction of rotation | Crankshaft clock-wise rotation (as viewed from output end) |
| Fuel consumption rate (When MCR happens) | 189g/kW.h，tolerance +5% |
| Air intake flow | 32.84kg/kW.h |
| Exhaust gas flow | 36.75t/ h |
| Exhaust gas temperature after supercharger | 350℃ |
| Supercharger air pressure | 3.04 bar |
| Supercharger air temperature before cylinder | 45~55℃ |
| Engine inlet lube pressure | 0.42~0.5MPa |
| Engine inlet lube temperature | 68~73℃ |
| H.T. water into-machine pressure | 0.2~0.5MPa |
| H.T. water out-machine temperature | 68~73℃ |
| L.T. water into-machine pressure | 0.25~0.45MPa |
| L.T. water into-machine temperature | 30~40℃ |
| Fuel into-machine pressure | 0.3~0.6MPa |

Alternator

| Brand | VEM/BEM |
| --- | --- |
| Rated power | 5700kW |
| Rated voltage | 11kV |
| Rated frequency | 50Hz |
| Rated speed | 750 r/min |
| Direction of rotation | Counter clock-wise (as viewed from input end) |
| PF | 0.8(Lagging) |
| Efficiency | 96% |
| Grade of Protection | IP23 |
| Winding temperature sensory | 2×6Pt100 (sensory) (1 set standby) |
| Anti-freezing heater | AC230V |
| Coolant method | Self-fan coolant |
| AVR (Automatic Voltage Regulator) | Installed on generator |

2.1.2  CSSC 8M3242

Double Fuel Gen -set T he generating sets mainly include engine , duplex bearing generator, high elasticity shaft coupling and public housing.D iesel and duplex  bearing generator are connected by high elasticity shaft coupling , which are also supported and fixed by common bed .

Function of generating sets:

Rated power ---------------------------------------------------------------4000kW

Rated speed ---------------------------------------------------------------750rpm

Rated voltage -------------------------------------------------------------- 1 1kV

Rated frequency -----------------------------------------------------------50Hz

PF(Power factor) ----------------------------------------------------------0.8    (lagging)

Boundary dimension) ---------------------------------------------------约10577×2736×5047    (mm)

D ry weight -------------------------------------------------------------------70 t

Steady-state voltage adjusting rate -----------------------------------≤2 .5%

Transient voltage adjusting rate ---------------------------------------+20%~-15%

Sudden load changing voltage steady time ------------------------ 1 .5S

Voltage fluctuation rate --------------------------------------------------0 .5%

Steady-state frequency adjusting rate -------------------------------≤ 0 .5%

Transient frequency adjusting rate -----------------------------------+ 10%~-7%

Sudden load changing frequency steady time ---------------------≤5S

Frequency fluctuation rate ----------------------------------------------≤ 0 .5%

Waveform distortion ------------------------------------------------------≤ 3%

Engine

| Brand and model of engine | CSSC 8M3242 |
| --- | --- |
| Pattern | L8 four stroke , direct injection turbocharger, water cooled , compressed air starting |
| Cylinder bore | 320mm |
| Stroke | 420mm |
| Compressed ratio | 15.2 |
| MCR (Most Continuous Power) | 4000kW |
| Speed | 750r/min |
| D irection of rotation | Crankshaft clock-wise rotation (as viewed from output end) |
| Fuel consumption rate (W hen MCR happens) | Oil:187g/kWh，gas:7.2KJ/kwh.tolerance +5% |
| Air intake flow | 37.4kg/kW .h |
| Exhaust gas flow | 40 .75t/ h |
| Exhaust gas temperature after supercharger | 350℃ |
| Supercharger air pressure | 3 .04 bar |
| Supercharger air temperature before cylinder | 45~55℃ |
| E ngine inlet lube pressure | 0 .42~ 0 .5MPa |
| E ngine inlet lube temperature | 68~73℃ |
| H .T . water into-machine pressure | 0 .2~0 .5MPa |
| H .T . water out-machine temperature | 68~73℃ |
| L .T . water into-machine pressure | 0 .25~0 .45MPa |
| L .T . water into-machine temperature | 30~40℃ |
| Fuel into-machine pressure | 0 .3~0 .6MPa |

Alternator

| Brand | ZFC/KFS |
| --- | --- |
| Rated power | 3500kW |
| Rated voltage | 11 kV |
| Rated frequency | 50Hz |
| Rated speed | 750 r/min |
| D irection of rotation | Counter clock-wise (as viewed from input end) |
| PF | 0 .8(Lagging) |
| Efficiency | 96% |
| G rade of P rotection | IP23 |
| W inding temperature sensory | 2 ×6Pt 100 (sensory) ( 1 set standby) |
| Anti-freezing heater | AC230V |
| Coolant method | Self-fan coolant |
| AVR (Automatic Voltage Regulator) | Installed on generator |

## 2.2MECHANICAL AUXILIARY SYSTEM

2.2.1 LUBRICATING OIL SYSTEM

The engine has it’s own internal lubricating oil system. Lube oil service tank is mounted on common-bed.

| Lube oil filter | Duplex type |
| --- | --- |
| Lube oil pump | Engine driven, mounted on engine |
| Lube oil cooler | Plate type, mounted on engine |
| Pre-lubricating pump | Electric Motor driven |
| Thermostatic valve | Mounted on engine |

2.2.2 COOLING WATER SYSTEM

The engine cooling water system consists of two cooling water circuits, which are Low temperature(LT) and High temperature(HT) water circuits. The heat transfer to engine cooling water is discharged to atmosphere by Radiator Cooling.

| Low temperature water circuit comprises: |  |
| --- | --- |
| LTCW pump | Mounted on engine |
| Charge air cooler | Mounted on engine |
| Lubricating oil cooler | Plate type |
| LTCW radiator | Air cooling |
| LTCW expansion water tank |  |
| High temperature water circuit comprises: |  |
| HTCW pump | Engine driven, mounted on engine |
| Engine water jackets/cylinder head | Mounted on engine |
| Thermostatic valve | Mounted on engine |
| HTCW expansion water tank |  |

2.2.4 COMPRESSED AIR SYSTEM

The compressed air supply system consists of starting air receiver and air compressor as follows.

The compressed air supply system provides also the control air to the related auxiliaries through pressure-reducing valve.

| Engine starting | Compressed air, 3/7 bar |
| --- | --- |
| Air compressor | Electric Motor driven, 30 bar |
| Air receiver | Cylindrical, 30 bar |

2.2.5INTAKE AIR SYSTEM

Intake air filter is dry and washable type filter to be mounted on turbocharger.

2.2.6 EXHAUST GAS SYSTEM

Exhaust gas of the engine flows out from turbocharger to atmosphere via expansion joint and silencer.

- Total pressure loss in the exhaust gas system : max. 2.5kPa

- Exhaust gas silencer : absorption & resonance Type

- Exhaust gas boiler unit : Smoke tube type,0.7 bar.

## 2.3 ELECTRICAL AUXILIARY SYSTEM

Electrical system mainly includes medium voltage system, low voltage system, control system, etc.

2.3.1PLANT SYSTEM VOLTAGE

| Generator | AC 11kV, 3PH, |
| --- | --- |
| Secondary distribution | AC 400V,3PH, |
| Motors | AC 400V,3PH, |
| AC control | AC 230V, 1PH, |
| DC control | DC 110V, 2W or 24V, |
| Grid | AC 90kV, 3PH, |

2.3.2 SWITCHGEARS

General description

- 11/90kV switchgear shall be indoor, metal-enclosed, floor mounted, draw out type.

Meters, relays, switches and lamps will be flush mounted on the respective cubicle door or on control cabinet. The degree of protection enclosure will be of IP 41x.

- The breakers shall be triple pole, single throw and vacuum circuit breaker

- All the external cables will enter the switchgear through adequate openings at the bottom.

- Current transformers(CT) will be epoxy-resin type. All current transformer secondary will be connected to short circuiting terminal blocks.

- Potential transformers(PT) will be epoxy-resin type with primary and secondary fuses.

- The accuracy class for CT & PT will be of 1.0 cl. for metering 5P20 for protection.

- The vacuum circuit breaker operating and control circuit will be for 110V DC supplied from 110V DC station which is normally floated with battery and battery charger.

- The switchgear cubicle will be provided with space heaters to prevent condensation of moisture within the switchgear.

- For generator feeders, the necessary electrical parameters are to be measured or displayed in each generator control panel.

Particulars

| Type | KYN28-24 |
| --- | --- |
| Rated voltage | 90kV 3PH, 50Hz |
| Service voltage | 11kV 3PH, 50Hz |
| Ground system | Solidly grounded |
| Control power | DC110V |
| Switch gear main bus current | 630A |
| Material of busbar | Copper |
| Circuit breaker | Type: Draw out type, VCB Rated voltage: 108kV, 3PH Rated current: 630A Rated interrupting current: 25kA |

2.3.3 400V SWITCHGEARS/MCC/DISTRIBUTION BOARDS

General description

- L.V switchgear will be metal-enclosed, free-standing, dead front structure with electrically operated draw out type air circuit breaker suitable for indoor installation.

- The air circuit breaker will be 3-pole, 600V class air circuit breaker (ACB) with suitable rating of continuous current rating and interrupting rating respectively.

Specification

| Type | Metal enclosed type for indoor service |
| --- | --- |
| Rated voltage | 600VAC,3PH,50Hz |
| Service voltage | 400VAC,3PH,50Hz |
| Ground system | Solidly grounded |
| Control power | 110VDC for ACB and 230VAC, 1Ph |
| Bus | Copper bus with current rating as required |
| Circuit breaker | Air circuit breaker |
|  | - Type : Draw out type - Rate voltage: 600V, 3PH, 50Hz - Rated current: 630A - Rated interrupting current : 65kA SYMM. - Operating type : Motor spring type - Over current trip : Direct acting trip device - No of poles: 3p |

2.3.5 POWER TRANSFORMER

Booster Particulars

| Transformer :Unit booster transformer 7sets : |  |
| --- | --- |
| a) Rated voltage |  |
| H.V | 90kV |
| L.V | 11kV |
| b) Winding |  |
| H.V | Delta |
| L.V | Wye |
| c) Vector group | Dyn11 |
| d) Capacity | 25MVA |
| e) Cooling | dry |
| f) Tap changer | NLTC 2 ×±2.5% TAPS |

Aux Particulars

| Aux. Transformer 2 sets |  |
| --- | --- |
| a) Rated voltage |  |
| H.V | 11kV |
| L.V | 0.4kV |
| b) Winding |  |
| H.V | Delta |
| L.V | Wye |
| c) Vector group | Dyn11 |
| d) Capacity | 1250kVA |
| e) Cooling | oil-immersed |
| f) Tap changer | NLTC 2 ×±2.5% TAPS |

2.3.6 DC SYSTEM

Batteries

| Rated voltage | 110V DC & 24V DC |
| --- | --- |
| Type | Lead-Acid |
| No. of cell | As required |
| Capacity | As required |
| No minal voltage | 12V/cell |
| Back-up time | 60 Minutes |
| * Capacity shall be adjusted during the detail design |  |

Battery Charger

| TYPE | Metal-enclosed, indoor, floor mounted Float charger combined booster charger |
| --- | --- |
| Quantity | One set for 110V DC system |
| Rated output | 24V DC, 50A & 110V DC, 50A |
| Feeder | Molded case circuit breaker |
| No. of pole | 2P |

2.3.7 MOTOR

General Description

- AC motors will be suitable for operation on 3-phase, 400V, 50Hz.

- Unless otherwise specified, all the AC motors will be squirrel cage induction motors suitable for full voltage direct starting.

| Technical Specifications for LV Motors. |  |
| --- | --- |
| Rated voltage | 400V, 3PH, 50Hz |
| Enclosure | Indoor area Outdoor area |
| Insulation class | F |
| Space heaters | Outdoor motors, 37.5KW & larger |
| Starting type | Direct on line starting |
| Others | Tropical design |

2.3.8 Cables

2.3.8.1 HV Power Cables

| Type | 24 kV, XLPE, PVC sheathed |
| --- | --- |
| Core | 3C |
| Minimum size | As per calculation |
| Conductor | Copper |

2.3.8.2 L.V Power Cables

| Type | 0.6/1.0kV XLPE, PVC sheathed |
| --- | --- |
| Core | Multiple (3C or 4C) |
| Conductor | Copper |

2.3.8.3 Control Cables

| Type | 600V CVV (PVC/PVC) |
| --- | --- |
| Shielding | As needed |
| Multiple Core | Multiple (2C through 30C) |
| Conductor | Copper |

2.3.8.4Instrumentation cables

| Type | 600V CVVS |
| --- | --- |
| Shielding | Shielded |
| Core | 1 pair and multi-pair |
| Conductor | Copper |

2.3.10 Conduits and trays

1) Cables will be installed in above ground conduits, cable trays, underground conduits

or cable trenches or direct buried.

2) Conduits will be rigid steel conduits.

3) Separate trays for instrumentation cables will be provided to separate them from

power cable.

4) Trays for cables for different voltage levels will be stacked in descending order with the

higher voltage above. Instrumentation trays will always be at the bottom.

5) Trays will be made of hot-dip galvanized steel for outdoor and indoor.

2.3.11.1 ENGINE/ GENERATOR CONTROL PANEL

Engine/ Generator control panel will be metal-enclosed, free-standing, IP40, indoor installation.

a) Control and Monitoring

- Engine RPM display

- T/C RPM display

- Engine pressure display

Starting air pressure

FO engine inlet pressure

LO engine inlet pressure

- Engine temperature display

FO engine inlet temperature

HT water outlet temperature

Exh. Gas T/C inlet temperature

- D/G set emergency stop

- Engine start and stop

- Engine speed control

- Generator voltage control

b) Annunciator

c) Synchronizing

d) Protection relay (Multi or single protective type)

- Under/ over voltage protection

- Reverse power protection

- Loss of excitation

- Over current protection

- Over current ground protection

- Under and over frequency protection

- Lock out relay(separate type)

- Differential Protective Relay(87G)

However, the above shall be adjusted subject to detail design

2.3.11.2 Field instrumentation

Necessary local instrumentation for field tanks and pipe lines will be provided properly for efficient and reliable plant operation, subject to our standard. Instrumentation will be tropicalized to suitable the conditions of the plant environment.

But, the instruments for tanks will be supplied by tanks supplier when tanks are out of contractor`s scope Wherever possible, instruments which perform similar functions in similar applications will be of uniform type and manufacturer. However package mounted instruments will be subject to manufacture standard and practice.

Each instrument will be identified and tagged with a tag number, according to job standards. Local indicators will be graduated to in engineering units of the measures variable. Instrument scale ranges will be expressed in S.I. Engineering units.

All the instruments will be the industrial type and field proven design.

| SCOPE OF SUPPLY FOR 150MVA Gen-set |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SU: Supply by Supplier; CT: Prepare by Buyer; |  |  |  |  |  |  |  |
| NO. | ITEM | SPECIFICATION | QTY. | UNIT | SCOPE |  | REMARKS |
|  |  |  |  |  | SU | CT |  |
| (A) | GENERATING SET |  |  |  |  |  |  |
| (A-1) | GENERATING SET |  | 30 | units | ■ |  |  |
|  | Engine |  | 30 | units |  |  |  |
|  | Flexible coupling | HGT | 30 | units |  |  |  |
|  | Alternator with AVR | 11kV 50Hz | 30 | units |  |  |  |
|  | Common base frame |  | 30 | units |  |  |  |
|  | Foundation bolts |  | 30 | units |  |  |  |
|  | Vibration isolator |  | 30 | units |  |  |  |
|  | Maintenance platform |  | 30 | units |  | ■ |  |
| (B) | DO FUEL OIL SYSTEM 柴油燃油系统 |  |  |  |  |  |  |
| (B-1) | DO Storage Tank | 200m³ vertical | 2 | unit |  | ■ |  |
| (B-2) | DO unloading unit | 2*20m³/h,2.5Bar | 2 | unit | ■ |  |  |
| (B-3) | Daily service tank | 20m³ horizontal | 2 | unit |  | ■ |  |
| (C) | HEAVY FUEL OIL (HFO) SYSTEM |  |  |  |  |  |  |
| (C-1) | HFO Storage Tank | 5000m³ | 6 | pcs |  | ■ |  |
| (C-2) | HFO unloading unit | 2*30m³/h,2.5Bar | 6 | unit | ■ |  |  |
| (C-3) | HFO sediment tank | 200m³ vertical | 4 | units |  | ■ |  |
| (C-4) | HFO daily tank | 200m³ | 4 | unit |  | ■ |  |
| (C-6) | HFO purified separator module |  | 12 | unit | ■ |  |  |
| (C-7) | Common Circulating & Booster module |  | 6 | unit | ■ |  |  |
| (C-8) | Gas system unit |  | 4 | unit | ■ |  |  |
| (C-9) | GVU |  | 30 | unit | ■ |  |  |
| (D) | Lubricating oil system unit |  |  |  |  |  |  |
| (D-1) | LO purifier separator |  | 30 | unit | ■ |  |  |
|  | Lubricating oil filling unit |  | 2 | set | ■ |  |  |
| (D-3) | Lubricating supply oil unit |  | 30 | sets | ■ |  |  |
| (E) | Compressed air system unit |  |  |  |  |  |  |
| (E-1) | Starting air compressor unit | Motor driven | 8 | units | ■ |  |  |
| (E-2) | Starting air compressor unit | Diesel engine driven | 1 | unit | ■ |  |  |
| (E-3) | Air Receiver unit | 500L 30bar | 8 | PCs | ■ |  |  |
| (F) | Cooling system unit |  |  |  |  |  |  |
| (F-1) | water Cooling |  | 30 | units | ■ |  |  |
| (F-2) | Low Cooling water pump | Motor driven type | 30 | sets | ■ |  |  |
| (F-3) | Water soften device |  | 6 | units | ■ |  |  |
| (G) | Exhaust gas and steam system |  |  |  |  |  |  |
| (G-1) | Exhaust gas silencer | 25dBA reduce | 30 | units | ■ |  |  |
| (G-2) | Expansion bellow |  | 30 | sets | ■ |  |  |
| (G-3) | exhaust boiler |  | 15 | units | ■ |  |  |
| (G-4) | SCR Tail gas treatment plant |  | 30 | units | ■ |  |  |
| (H) | Eectrical system |  |  |  |  |  |  |
| (H-1) | Genset switchgear | KYN28A 630A | 30 | units | ■ |  |  |
| (H-2) | Linkage panel for generating | KYN28A | 3 | unit | ■ |  |  |
| （H-3） | Station transformer panel | 11/√3, 0.1/√3, 0.1/3 kV | 3 | Pcs |  |  |  |
| H-4 | PT panel | 19/45 | 3 | Pcs |  |  |  |
| H-5 | Plant transformer (1250kVA 11KV//0.4KV) |  | 4 | Pcs |  |  |  |
| H-6 | 400 Volt main panel | with phase change switch | 3 | Pc |  |  |  |
| H-7 | Out switchgear |  | 15 | Pc |  |  |  |
| H-8 | Gen-set auot Synchronous | KYN28A 630A | 3 | unit | ■ |  |  |
| H-9 | DC System |  | 3 | unit |  |  |  |
| H-10 | Local control cabinet | VS1 630A 25KA | 30 | set |  |  |  |
| H-11 | Centralized console |  | 3 | units | ■ |  |  |
| H-12 | 90KV booster station 11/90KV 25MVA |  | 7 | units | ■ |  |  |
|  | (1)hight voltage switchgear 11/90kv 25MVA |  | 7 | units |  |  |  |
|  | (2) 90KV transformer 11/90KV 25MVA |  | 7 | units |  |  |  |
| (L) | Power Plant control |  |  |  |  |  |  |
| (L-1) | Air compressor control box |  | 1 | units | ■ |  |  |
| (L-2) | Gen-set Aux. Control Panel | KCT | 1 | units | ■ |  |  |
| (L-3) | Fuel oil field power panel | XL-21 | 1 | unit | ■ |  |  |
| (L-4) | Seperator power panel | XL-21 | 1 | unit | ■ |  |  |
| (L-5) | Power plant aux. panel |  | 1 | units | ■ |  |  |
| (O) | Power plant ventilation and lighting |  |  |  |  |  |  |
| (O-1) | Power plant ventilation |  | 40 | lot |  | ■ |  |
| (O-2) | Lighting |  | 40 | lot |  | ■ |  |
| (P) | Overhead Crane |  |  |  |  |  |  |
| (P-1) | Overhead crane | 75/10T | 4 | set |  | ■ |  |
| (Q) | Fire fighting system |  |  |  |  |  |  |
| (Q-1) | Fire hose and Fire gun |  | 20 | lot |  | ■ |  |
| (Q-2) | Portable chemical fire extinguishers |  | 32 | lot |  | ■ |  |
| (Q-4) | sand bucket |  | 32 | lot |  | ■ |  |
| (R) | Installation material |  |  |  |  |  |  |
|  | Mechanical installation materials |  |  |  |  |  |  |
| (R-1) | Valves, pipings, flange |  | 1 | lot | ■ |  |  |
| (R-2) | Connection bolts and nut |  | 1 | lot | ■ |  |  |
| (R-3) | Mechanial installation tools |  | 1 | lot | ■ |  |  |
| (R-4) | Paint, electrical rod |  | 1 | lot | ■ |  |  |
| (R-5) | Heat insulation rock wool & metal claddings |  | 1 | lot | ■ |  |  |
| (R-6) | Power plant lightning protection |  | 1 | lot | ■ |  |  |
| (R-7) | Earthling system |  | 1 | lot | ■ |  |  |
|  | Electrical installation materials |  |  |  |  |  |  |
| (R-8) | Lamps and lanterns,emergency lighting |  | 1 | lot | ■ |  |  |
| (R-9) | HV cable,LV cable,control cables, wires & termination lugs |  | 1 | lot | ■ |  |  |
| (R-10) | LV power cables termination lugs |  | 1 | lot | ■ |  |  |
| (R-11) | HT power cables & termination kits |  | 1 | lot | ■ |  |  |
| (R-12) | Cable tray, ladders, and support structures |  | 1 | lot | ■ |  |  |
| (R-13) | Painting - cable tray, ladders, and support structures |  | 1 | lot | ■ |  |  |
| (R-14) | Cable fireproofing materials |  | 1 | lot | ■ |  |  |
| (R-15) | Test equipments |  | 1 | lot | ■ |  |  |
| (S) | Commissioning consumptions |  |  |  |  |  |  |
| (S-1) | Acid for piping wash | HCl | 1 | lot |  | ■ |  |
| (S-2) | Engine lubricating oil | SAE 15WCD40 | 1 | lot |  | ■ |  |
| (S-3) | Diesel oil /HFO |  | 1 | lot |  | ■ |  |
| (S-4) | Grease | Lithium base 3#锂基3# | 60 | kg |  | ■ |  |
| (S-5) | Water |  | 1 | lot |  | ■ |  |
| T | Emergency genset 200kw 400v |  | 1 | set | ■ |  |  |
| U | Spare parts , Documents |  | 2 | set | ■ |  |  |
| V | special tools |  | 2 | set | ■ |  |  |
| W | Steel structure generator room |  | 1 | set |  | ■ |  |
|  | steel structure |  | 1 | set |  | ■ |  |
|  | Embedded steel plate |  | 1 | set |  | ■ |  |
|  | Civil engineering |  | 1 | set |  | ■ |  |