## Quotation
7×2195kW重油电站设备报价 Power Plant 7×2195kW Equipment Quotation
序号 No. | 设备名称 Equipment | 数量 Qty | 单位 Unit | 单价 Unit Price (USD) | 总价 Total Price (USD) | 备注 Remark
1 | 柴油发电机组 2195kW 11KV/50Hz Standard 2195kW/11KV/50Hz generating set | 7 | sets |  | 0
1.1 | 中速柴油机 MAN 7L27/38 2310kW@750rpm Engine MAN 7L27/38 2310kW@750rpm | 7 | pcs
1.2 | 柴油机附属设备 Diesel engine accessory equipments | 7 | sets
1.3 | 发电机 11kV 10P IP23 750rpm Three phase syn. brushless alternator | 7 | pcs
1.4 | 机组高压开关柜 Gen-set Switchgear | 7 | pcs |  |  | KYN28-12，带继保
1.5 | 机组集控台 Gen-set control board | 7 | pcs
1.6 | 机组机旁台 Gen-set local control desk | 7 | pcs
1.7 | 共同底座及联轴器 Common base frame and flexible coupling | 7 | sets
1.8 | 弹性安装减震块 Semi-block damper | 7 | sets
1.9 | 基础螺栓 Foundation Bolts | 7 | sets
2 | 电站机组外围机械设备 Power Plant Auxiliary Equipment | 7 | lot |  | 0
2.1 | 排气消音器 Exhaust silencer | 7 | pcs
2.2 | 膨胀节 Expansion joint | 7 | pcs
2.3 | 排气管 Exhaust piping | 7 | sets
2.4 | 冷却塔 Cooling Tower | 7 | pcs
2.5 | 高温水膨胀水箱 HT water expansion tank | 7 | pcs
2.6 | 外置润滑油箱 2000L带阀门 External lubricating oil tanker | 7 | pcs
2.7 | 管道旁通离心滤器 Bypass type centrifugal separator | 7 | pcs
2.8 | 滑油液位指示器 Lubricating oil level indication | 7 | sets
2.9 | 电站移动润滑油泵 Power plant dolly LO pump | 1 | set
2.1 | 电动空压机组 Electrical motor driven air compressor | 3 | pcs
2.11 | 柴油机空压机组 Diesel engine driven air compressor | 1 | pc |  |  | 295柴油机带
2.12 | 压缩空气瓶 Compressed air receiver | 6 | pcs
2.13 | 进气滤系统 Air intake system | 7 | sets |  | 0
3 | 电站电气动力柜 Power Plant Electrical Panel | 1 | lot
3.1 | 11KV 电站母线压变柜 11KV Busbar PT panel | 1 | Set |  | 0
3.2 | 电站1000V总出线柜 1250A VS1-12 Power Plant 1000V Main Outgoing panel | 5 | Sets |  | 0
3.3 | 电站所用变出线柜 Power Plant aux. transformer panel | 1 | Set |  | 0
3.4 | 电站低压总柜 （GCS柜） 400V LV Main Panel | 1 | Set |  | 0
3.5 | 电站低压柜 （GCS柜） 400V LV distribution Panel | 4 | Sets |  | 0
3.6 | 电站直流电源 DC Power for power plant | 1 | Set |  | 0
3.7 | 电站500kVA所用变 500kVA Station Transformer 1000/400V S11-M | 1 | Set |  | 0 | S11
3.8 | 油库动力箱 400 Volt supply panel for fuel station | 1 | Pc |  | 0
3.9 | 锅炉控制箱 BOILER CONTROL BOX | 1 | Pc |  | 0
3.1 | 空压机控制箱 AIR COMPRESSOR CONTROL BOX | 1 | Pc |  | 0
3.11 | 污油泵控制箱 SEWAGE PUMP CONTROL BOX | 1 | Pc |  | 0
3.12 | 电站检修动力箱 Power plant maintenance cabinet | 3 | Pcs |  | 0
4 | 油处理设备 OIL Treatment Equipment | 1 | lot
4.1 | 重油分离机组 HFO Purified Separator module | 1 | Set |  | 0
4.1.1 | 自动重油分离机组 HFO separator set | 1 | Set
4.1.2 | 分离机组控制箱 Separator set control box | 1 | Set
4.1.3 | 渣油箱及渣油泵 Sludge oil tank and sludge pump | 1 | Set
4.2 | 供油单元 Fuel booster module | 1 | Set |  | 0
4.2.1 | 重油循环油泵（日用重油箱到柴油机） HFO circulating pump | 1 | Set
4.2.2 | 重油压力调节阀 HFO pressure regulating valve | 1 | Set
4.2.3 | 重油流量表（带滤器） HFO flow meter (with strainer) | 1 | Set
4.2.4 | 粘度控制器+执行阀 Viscosity controller & Valve control | 1 | Set
4.2.5 | 混合油桶 Mixing barrel | 1 | Set
4.2.6 | 自动反冲洗滤器 Self clean filter | 1 | Set
4.2.7 | 控制箱 Control Box | 1 | Set
4.3 | 滑油分离机 Lubricating oil purified separator | 2 | Set |  | 0
4.3.1 | 自动分离机组 LO separator | 2 | Set
4.3.2 | 分离机组控制箱 Separator set control box | 2 | Set
4.4 | 导热油锅炉 Heat transfer oil boiler | 2 | Set |  | 0
4.5 | 导热油 Heat transfer oil | 12 | m³ |  | 0
4.6 | 重油卸油模块 HFO unloading and transfer pump unit with flow meter | 1 | Set |  | 0
4.6.1 | 卸油泵 Gear Pump | 2 | Sets
4.6.2 | 滤器 Filter | 1 | Set
4.6.3 | 流量计 Flow Meter | 1 | Set
4.6.4 | 阀门、管道 Valves and Pipings | 1 | Set
4.6.5 | 马达控制箱 MCU panel | 1 | Pc
4.7 | 柴油卸油模块 DO unloading and transfer pump unit with flow meter | 1 | Set |  | 0
4.7.1 | 卸油泵 Gear Pump | 2 | Sets
4.7.2 | 滤器 Filter | 1 | Set
4.7.3 | 流量计 Flow Meter | 1 | Set
4.7.4 | 阀门、管道 Valves and Pipings | 1 | Set
4.7.5 | 马达控制箱 MCU panel | 1 | Pc
5 | Water soft-treatment equipment 软水处理系统 | 1 | Set |  | 0
5 | 机械材料(仅包括连接供方提供设备之间互联所必须的机械安装材料，如管道、法兰、接头等） Mechanical installation materials （only include necessary installation materail e.g. pipes, flanges and joints etc. for connection among equipments provided by the supplier） | 7 | lot |  | 0
6 | 电气安装材料(仅包括连接供方提供电气设备安装材料，如电线电缆等，发电机出线电缆等） Electrical installation materials (only include necessary materail e.g. wires and cables etc. for connection among equipments provided by the supplier） | 7 | lot |  | 0
7 | 机组随机备件 Gen-set Spare parts | 7 | lot |  | 0
8 | 专业工具 Special tools | 3 | lot |  | 0
9 | 文件 Documents | 7 | lot |  | 0
10 | 安装工具及测试工具 Installation tools and testing tools | 1 | set |  | 0
11 | 安装耗材等 Installation consumables, etc | 1 | set |  | 0
| Total |  |  |  | 0
Notes
1. 所有报价基于Fob 宁波.
All prices are based on Fob Ningbo port.
2. 提供交货后1年或累计运转2000小时质量保证，以先到为准。
Quality guaranty: Provide full warranty within one year or 2000 operating hours from the date of delivery which ever comes earlier applies.
3. 交货期：收到预付款后十个月内。
Date of delivery: 10 months after date of deposite.
4. 付款方式：30%预付款，70%交货前15个工作日支付。
Payment: 30 percent advance payment, 70 percent before 15 working days delivery.
5. 报价有效期为2023年10月30日前。
Valid date for the offer: before Oct. 30, 2023
6. 安装指导及调试
Installation guide and test
a.供方派遣2-4名工程师到现场指导安装和调试，为期约3个月。需方应支付供方工程师每人每天1000美元津贴。
The supplier will dispatch 2-4 engineers to guide installation and commissioning on site that will take about 3 month. The buyer shall pay an allowance of USD 1000 per day for one engineer during that period.
b.供方派遣2名工程师到现场培训和运行指导，为期约1个月。需方应支付供方工程师每人每天1000美元津贴。
The supplier will dispatch 2 engineers to train and guide operation on site that will take about 1 month. The buyer shall pay an allowance of USD 1000 per day for one engineer during that period.
c.供方工程师国内外往返机票、工作地的食宿、交通、医疗等由需方承担。
The home and abroad round trip ticket, lodging, food, traffice and medical treatment for the supplier engineers shall be borne by customer.

## Technical parameters
2195GF1-3发电机组技术参数 Technical specificaiton for 2195GF1-3 Gen-sets
Ⅰ. 发电机组技术参数 Ⅰ. Gen-set technical specification
序号 No. | 项目 Item | 单位 Unit | 规格 Specification
1 | 型号 Model |  | 2195GF
2 | 额定功率 Rated power | kW | 2195
3 | 额定转速 Rated rev. | rpm | 750
4 | 额定电压 Rated voltage | V | 11000
5 | 额定电流 Rated current | A | 144.0138
6 | 频率 Frequency | Hz | 50
7 | 功率因素 Power factor |  | 0.8 (lagging)延迟
8 | 相位 Phase |  | 3-phase
9 | 电压波动率 Voltage fluctuation rate | % | ±1
10 | 频率波动率 Frequency (rev.) fluctuation rate | % | ±0.5
11 | 稳态调压率 Stable voltage regulating rate | % | ±2.5
12 | 稳态频率调整率 Stable frequency (rev.) regulating rate | % | 5
13 | 瞬时频率（rev.）调节率 Transient frequency (rev.) regulating rate | % | ±20～-15
14 | 稳定时间 Stabilizing time | s | 5
15 | 电压调整方式 Voltage regulating method |  | 自动 Auto
16 | 调速器 Speed Governor |  | 电液调速器 Electrical hydraulic
17 | 频率调整方式 Frequency regulating method |  | 自动 Auto
18 | 润滑方式 Lubricating method |  | 压力润滑 Pressure lubricating
19 | 冷却方式 Cooling method |  | 闭式淡水冷却 Close circuit of fresh cooling water
20 | 联轴器 Coupling |  | 高弹 Flexiable
21 | 油漆颜色 Painting color |  | 蓝色 Blue
22 | 外形尺寸 Overall dimension | mm | 8002*2420*3899 mm
23 | 净重 Net weight | kg | 51000
Ⅱ.柴油机参数 Ⅱ. Diesel engine specification
序号 No. | 项目 Item | 单位 Unit | 规格 Specification
1 | 发动机型号 Engine Model |  | MAN 7L27/38
2 | 型式 Type |  | 直列，7缸，四冲程，直喷，增压，中冷 In-line, 7-Cyls, four-stroke, direct injection, charged, inter cooled
3 | 缸径 Bore | mm | 270
4 | 行程 Stroke | mm | 380
5 | 排量 Total displacemen | L | 151.9
6 | 平均活塞速度 Mean piston seed | m/s | 9.5
7 | 额定功率 Rated power | KW | 2130
8 | 额定转速 Rated rev. | rpm | 750
9 | 超负荷运行 Overload (1 hr per 12 hrs) | kW/rpm | 2343/750
10 | 平均有效压力 Mean effective pressure | MPa | 2.43
11 | 压缩比 Compression ratio |  | 13
12 | 转向 Rotation direction |  | 顺时针，面朝飞轮端 Clockwise, viewed from flywheel end.
13 | 发火顺序 Firing order |  | 1-2-4-6-7-5-3
14 | 燃油消耗率 Specific fuel oil consumption | g/kW.h | 184+5%
15 | 滑油消耗率 Specific Lube oil consumption | g/kW.h | < 0.8
16 | 烟色 Smoke | RB | ≤0.3
17 | 噪音 Noise | dB(A) | 105
18 | 启动方式 Starting method |  | 气启动 Air Rotary valve
19 | 冷却系统 Cooling system |  | 淡水冷却 Fresh water cooling
20 | 润滑系统 Lubricating system |  | 压力润滑 Pressure lubricating
21 | 燃油规格 Fuel oil specification |  | 柴油 Diesel oil
22 | 滑油规格 Lube oil specification |  | CD40 with TBN according HFO
23 | 活塞吊缸高度 Piston lifting height | mm | 2600
24 | 外形尺寸 Overall dimension | mm | 5236*2420*3899 mm
25 | 净重 Net weight | kg | 33000
Ⅲ. 发电机参数 Ⅲ. Alternator specification
序号 No. | 项目 Item | 单位 Unit | 规格 Specification
1 | 发电机型号 Alternator Model |  | TF 2195（利莱森玛）
2 | 类型 Type |  | 无刷电机 Brushless generator
3 | 额定功率 Rated power | kW | 2195
4 | 额定电压 Rated voltage | V | 11000
5 | 额定电流 Rated current | A | 144.0138
6 | 频率 Frequency | Hz | 50
7 | 功率因素 Power factor |  | 0.8 (lagging)延迟
8 | 工作方式 Working condition |  | 连续运行 Continuous
9 | 相位和连接 Phase and connection |  | 3相6线 3-phase, 6-wires
10 | 电压调整方式 Voltage regulation method |  | 无刷，自励磁 Brushless, self excited
11 | 绝缘等级 Insulation Class |  | F
12 | 保护等级 Protection Class |  | IP23
13 | 电机效率 Efficiency |  | 95%
Remark:
1. Rating for marine genset are based on the standard environment conditions： Ambient temperature：45℃； Total barometric pressure：100kPa； Charge air coolant temperature：32℃； Relative humidity：30%。 If the test ambient conditions are not same as the standard ambient conditions, the power and fuel consumptions should be revised according to ISO-3046.
2. The Gen-set is allowed to run continuously or intermittently with 110% rated power for 1 hour every 12 hours.

## Spare parts
附件1：L27/38标准备件清单 Genset L27/38 Standard Spare Parts’ List
单套清单如下 One set of list as follow:
No. | Description | Plate | Item | Qty. per set
序号 | 描述 | 图册号 | 件号 | 数量/套
Cylinder Head 气缸盖：
1 | Valve seat ring, inlet 进气阀座 | 50501 | 123 | 2
2 | O-ring O形圈 | 50501 | 172 | 2
3 | Valve seat ring, outlet 排气阀座 | 50501 | 184 | 4
Valve spindles and valve gear 气阀和阀传动机构：
4 | Conical ring 锁夹 | 50502 | 178 | 6
5 | Rotocap complete 转帽 | 50502 | 191 | 6
6 | Spring 弹簧 | 50502 | 201 | 6
7 | Valve spindle, outlet 排气阀 | 50502 | 262 | 4
8 | Valve spindle, inlet 进气阀 | 50502 | 274 | 2
Piston and connecting rod 活塞和连杆：
9 | Piston ring packet 活塞环组 | 50601 | 306 | 1
10 | Piston pin 活塞销 | 50601 | 19 | 1
11 | Retaining ring 挡圈 | 50601 | 32 | 2
12 | Bush for connecting rod 连杆衬套 | 50601 | 56 | 1
13 | Connecting rod bearing 2/2 连杆瓦 | 50601 | 139 | 1
14 | Screw for connecting rod 连杆螺栓 | 50601 | 152 | 2
15 | Nut 螺母 | 50601 | 164 | 2
16 | Screw for connecting rod 连杆螺栓 | 50601 | 211 | 4
17 | Nut 螺母 | 50601 | 188 | 4
Frame with main bearings 机架及主轴瓦：
18 | Main bearing shell, 2/2 主轴瓦 | 51104 | 21 | 1
19 | Thrust bearing ring 止推片 | 51104 | 33 | 2
Fuel injecting pump 喷油泵：
20 | Fuel injecting pump, complete 喷油泵 | 51401 | 565 | 1
Fuel injection valve 喷油器：
21 | O-ring O形圈 | 51402 | 33 | 5
22 | O-ring O形圈 | 51402 | 189 | 5
23 | Fuel valve 喷油器 | 51402 | 116 | 5
Fuel injection pipe 高压油管：
24 | Fuel injection pipe, complete 高压油管 | 51404 | 117 | 1
Cooling water connections 冷却水接口：
25 | Seal ring 密封圈 | 51630 | 212 | 8
Gaskets 垫片：
26 | Kit for cylinder unit气缸单元垫片配件 | 51704 | 21 | 1
Turbocharger System增压系统：
27 | Standard spare parts’ kit for turbocharger增压器标准备件包 |  |  | 1

## Tools and documents
L27/38正常维修的标准工具清单 Genset L27/38 Standard Tools’ List for Normal Maintenance
No. | Description | Qty. per set | Plate No. | Item No.
序号 | 名 称 | 数量/套 | 图册号 | 件号
Cylinder head 气缸盖：
1 | Valve spring tightening device 气阀弹簧拆装工具 | 1 | 52000 | 14
2 | Lifting tool for cylinder unit 气缸单元起吊工具 | 1 | 52000 | 38
3 | Grinding tool for cylinder head/liner 气缸盖和气缸套研磨工具 | 1 | 52002 | 126
4 | Max. pressure indicator爆压表 | 1 | 52002 | 138
5 | Handle for indicator valve示功阀手轮 | 1 | 52002 | 498
Piston, connecting rod and cylinder liner
活塞，连杆和气缸套：
6 | Removing device for flame ring 火焰圈拆卸工具 | 1 | 52000 | 21
7 | Guide bush for piston 活塞导向圈 | 1 | 52000 | 45
8 | Fit and removal device for conn. rod bearing | 1 | 52000 | 69
连杆大头拆装工具
9 | Lifting device for cylinder liner 气缸套起吊工具 | 1 | 52000 | 82
10 | Lifting device for piston and connecting rod | 1 | 52000 | 104
活塞,连杆组吊装工具
11 | Testing mandrel for piston ring grooves, 6.43 mm | 1 | 52002 | 151
活塞环槽塞规
12 | Testing mandrel for piston ring grooves, 8.43 mm | 1 | 52002 | 163
活塞环槽塞规
13 | Piston ring opener 活塞环扩张钳 | 1 | 52000 | 190
14 | Supporting device for connecting rod and piston in the cylinder liner 活塞连杆、气缸套安装工具 | 1 | 52000 | 212/221
Operating gear for inlet and exhaust valves
进、排气阀传动机构：
15 | Feeler gauge 塞尺 | 1 | 52000 | 10
16 | Socket wrench and Torque Spanner气阀间隙调整工具 | 1 | 52000 | 652,
664
676
Crankshaft and main bearings 曲轴和主轴瓦:
17 | Dismantling tool for main bearing upper shell | 1 | 52000 | 35
上轴承瓦拆卸工具
18 | Tool for fixing of marine head for counterweight | 1 | 52000 | 60
连杆大头固定工具
Turbocharger system 增压系统:
19 | Container complete for water washing of compressor side | 1 | 51205 | 318
压气机水洗工具
20 | Blowgun for dry cleaning of turbocharger涡轮干洗喷枪 | 1 | 51210 | 136
21 | Wet cleaning device for turbo side涡轮侧水洗工具 | 1 | 52000 | 481
22 | Standard tools’ kit for turbocharger 增压器标准工具包 | 1
Fuel oil system 燃油系统:
23 | Cleaning tool for fuel injector 喷油器清理工具 | 1 | 52000 | 13
24 | Pressure testing tool 喷油器试验台 | 1 | 52000 | 50
25 | Grinding device for nozzle seat 喷油器座研磨工具 | 1 | 52000 | 74
26 | Extractor device for injector valve 喷油器拉拔工具 | 1 | 52000 | 407
27 | Eye screw for lifting lubricating oil cooler | 1 | 52000 | 32
滑油冷却器吊环螺钉,M20
28 | Combination spanner, 36 mm 两用扳手 36mm | 1 | 52000 | 772
29 | Crow foot, 36 mm高压油管拧紧手柄 | 1 | 52000 | 784
Lubrication oil system 滑油系统:
30 | Eye screw for lifting of charge air cooler 空冷器吊环螺钉,M12 | 1 | 52000 | 36
Hydraulic tools 液压工具:
31 | Hydraulic tools complete | 1 | 52000 | 806
液压工具总成
32 | Air driven high pressure pump for hydraulic valve | 1 | 52002 | 653
风动液压泵
Other tools 其他工具:
33 | Crankshaft alignment gauge 曲轴甩档表(65-150mm) | 1 | 52002 | 67
34 | Lifting tool for engine complete 整机起吊工具 | 1