## Quotation
Date:20221110 |  |  |  |  | Ref.No.: 20221110PAK-A
Offer for 5×2MW HFO power plant
No. | Equipment | Qty | Unit | Unit Price (USD) | Total Price (USD) | Remark
1 | 柴油发电机组 2000kW /11KV/50Hz Standard 2MW/11KV/50Hz gen-set | 5 | sets | 470664 | 2353320
1.1 | 中速柴油机 Engine G8300 2206kW@600rpm | 5 | sets
1.2 | 柴油机附属设备 Diesel engine accessory equipments | 5 | lots
1.2.1 | 机带高温循环水泵 Engine driven HT circulating water pump | 5 | pcs
1.2.2 | 机带低温循环水泵 Engine driven LT circulating water pump | 5 | pcs
1.2.3 | 机带润滑油泵 Engine driven LO pump | 5 | pcs
1.2.4 | 扭震减振器 Torsional vibration damper | 5 | pcs
1.2.5 | 调速器 Speed governor | 5 | pcs
1.2.6 | 增压器 Turbocharger | 5 | pcs
1.2.7 | 中冷器 Intercooler | 5 | pcs
1.2.8 | 燃油滤清器 Fuel strainer | 5 | pcs
1.2.9 | 预润滑电动油泵 Prelubricating LO pump | 5 | pcs
1.2.10 | 水温控制阀 Water thermostatic valve | 5 | pcs
1.2.11 | 高温淡水冷却器 HT Water Cooler | 5 | pcs
1.2.12 | 滑油控制阀 Lubricating oil thermostatic valve | 5 | pcs
1.2.13 | 润滑油冷却器 Lubricating oil Cooler | 5 | pcs
1.2.14 | 机旁仪表控制台 Local control desk | 5 | pcs
1.2.15 | 滑油滤清器 Lubricating oil filter | 5 | pcs
1.2.16 | 滑油压力控制阀 Lubricating oil pressure control valve | 5 | pcs
1.3 | 发电机 11KV 10P IP23 600rpm Three phase syn. brushless alternator | 5 | sets
1.4 | 机组高压开关柜 Gen-set Switchgear | 5 | sets |  |  | KYN28，带继保
1.5 | 机组集控台 Gen-set control board | 5 | sets
1.6 | 机组机旁台 Gen-set local control desk | 5 | sets
1.7 | 共同底座及联轴器 Common base frame and flexible coupling | 5 | sets
1.8 | 电动空压机组 Electrical motor driven air compressor | 2 | sets
1.9 | 柴油机驱动空压机组 Engine motor driven air compressor | 1 | set
1.1 | 压缩空气瓶 Compressed air receiver | 5 | sets
2 | 电站机组外围机械设备 Power Plant Auxiliary Equipment | 5 | lots | 19440 | 97200
2.1 | 排气消音器 Exhaust silencer | 5 | pcs
2.2 | 膨胀节 Expansion joint | 5 | pcs
2.3 | 排气管 Exhaust piping | 5 | lots
2.4 | 冷却塔 Cooling Tower | 5 | pcs
2.5 | 高温水膨胀水箱 HT water expansion tank | 5 | pcs
2.6 | 冷却模块 Cooling Moduel | 5 | pcs
2.7 | 管道旁通离心滤器 Bypass type centrifugal separator | 5 | pcs
2.8 | 滑油液位指示器 Lubricating oil level indication | 5 | sets
2.9 | 电站移动润滑油泵 Power plant dolly LO pump | 2 | set
3 | 电站电气动力柜 Power Plant Electrical Panel | 1 | lot
3.1 | 11KV 电站母线压变柜 11KV Busbar PT panel | 1 | pc | 10044 | 10044
3.2 | 电站11KV总出线柜 1250A VS1-12 Power Plant 11KV Main Outgoing panel | 4 | pcs | 13176 | 52704
3.3 | 电站所用变出线柜 Power Plant aux. transformer panel | 1 | pc | 13176 | 13176
3.4 | 电站低压总柜 （GCS柜） 400V LV Main Panel | 1 | pc | 10044 | 10044
3.5 | 电站低压柜 （GCS柜） 400V LV distribution Panel | 2 | pcs | 8640 | 17280
3.6 | 电站直流电源 DC Power for power plant | 1 | set | 19440 | 19440
3.7 | 电站500kVA所用变 500kVA Station Transformer | 1 | pc | 11880 | 11880 | S11
3.8 | 电站机组自动并机及负荷分配系统 Gen-set Syn. Parallel and load sharing | 1 | pc | 9288 | 9288
3.9 | 油库动力箱 400 Volt supply panel for fuel station | 1 | pc | 1836 | 1836
3.1 | 锅炉控制箱 BOILER CONTROL BOX | 1 | pc | 540 | 540
3.11 | 空压机控制箱 AIR COMPRESSOR CONTROL BOX | 1 | pc | 540 | 540
3.12 | 污油泵控制箱 SEWAGE PUMP CONTROL BOX | 1 | pc | 540 | 540
3.13 | 电站检修动力箱 Power plant maintenance cabinet | 5 | pcs | 540 | 2700
4 | 重油处理设备 HFO Treatment Equipment | 1 | lot
4.1 | 重油分离机组 HFO Purified Separator module | 1 | set | 70200 | 70200
4.1.1 | 自动重油分离机组 HFO separator set
4.1.2 | 分离机组控制箱 Separator set control box
4.1.3 | 渣油箱及渣油泵 Sludge oil tank and sludge pump
4.2 | 供油单元 Fuel booster module | 1 | set | 66960 | 66960
4.2.1 | 重油循环油泵（日用重油箱到柴油机） HFO circulating pump
4.2.2 | 重油压力调节阀 HFO pressure regulating valve
4.2.3 | 重油流量表（带滤器） HFO flow meter (with strainer)
4.2.4 | 粘度控制器+执行阀 Viscosity controller & Valve control
4.2.5 | 混合油桶 Mixing barrel
4.2.6 | 自动反冲洗滤器 Self clean filter
4.2.7 | 控制箱 Control Box
4.3 | 滑油分离机 Lubricating oil purified separator | 2 | sets | 21600 | 43200
4.3.1 | 自动分离机组 LO separator
4.3.2 | 分离机组控制箱 Separator set control box
4.4 | 导热油锅炉 Heat transfer oil boiler | 2 | sets | 28080 | 56160
4.5 | 导热油 Heat transfer oil | 9 | m³ | 3024 | 27216
4.6 | 重油卸油模块 HFO unloading and transfer pump unit with flow meter | 1 | set | 14688 | 14688
4.6.1 | 卸油泵 Gear Pump | 2 | sets
4.6.2 | 滤器 Filter | 1 | pc
4.6.3 | 流量计 Flow Meter | 1 | pc
4.6.4 | 阀门、管道 Valves and Pipings | 1 | lot
4.6.5 | 马达控制箱 MCU panel | 1 | pc
4.7 | 柴油卸油模块 DO unloading and transfer pump unit with flow meter | 1 | set | 10800 | 10800
4.7.1 | 卸油泵 Gear Pump | 2 | sets
4.7.2 | 滤器 Filter | 1 | pc
4.7.3 | 流量计 Flow Meter | 1 | pc
4.7.4 | 阀门、管道 Valves and Pipings | 1 | lot
4.7.5 | 马达控制箱 MCU panel | 1 | pc
5 | Water soft-treatment equipment 软水处理系统 | 1 | set | 4320 | 4320
6 | 机械材料(仅包括连接供方提供设备之间互联所必须的机械安装材料，如管道、法兰、接头等） Mechanical installation materials （only include necessary installation materail e.g. pipes, flanges and joints etc. for connection among equipments provided by the supplier） | 5 | lot | 22680 | 113400
7 | 电气安装材料(仅包括连接供方提供电气设备安装材料，如电线电缆等，发电机出线电缆等） Electrical installation materials (only include necessary materail e.g. wires and cables etc. for connection among equipments provided by the supplier） | 5 | lot | 21600 | 108000
8 | 随机备件(标准供货） Spare parts | 5 | lot | 0 | 0
9 | 专用工具 Special tools | 2 | lot | 0 | 0
10 | 文件 Documents | 1 | lot | 0 | 0
| 合计 Total |  |  |  | 3115476
Notes
1. 所有报价基于FOB宁波。
All prices are based on FOB ningbo.
2. 提供交货后一年或累计运转2000小时质量保证，以先到为准。
Quality guaranty: Provide full warranty within one year or 2000 operating hours from the date of delivery which ever comes earlier applies.
3. 交货期：收到预付款后6个月内。
Date of delivery:6 months after date of deposite.
4. 付款方式：30%预付款，70%发货前支付。
Payment:30% advance payment, 70% before delivery.
5. 报价有效期为2022年12月30日前。
Valid date for the offer: before Dec. 30, 2022
6. 安装指导及调试
Installation guide and test
a.供方派遣5名工程师到现场指导安装和调试，为期约3个月。需方应支付供方工程师每人每天150美元津贴。
The supplier will dispatch 5 engineers to guide installation and commissioning on site that will take about 3 months. The buyer shall pay an allowance of USD150 per day for one engineer during that period.
b.供方派遣2名工程师到现场培训和运行指导，为期约1个月。需方应支付供方工程师每人每天150美元津贴。
The supplier will dispatch 2 engineers to train and guide operation on site that will take about 1 month. The buyer shall pay an allowance of USD 150 per day for one engineer during that period.
c.供方工程师国内外往返机票、工作地的食宿、交通、医疗等由需方承担。
The home and abroad round trip ticket, lodging, food, traffice and medical treatment for the supplier's engineers shall be borne by customer.

## Technical parameters
Technical specificaiton for 2000GF1-3 Gen-sets
Ⅰ. Gen-set technical specification
No. | Item | Unit | Specification
1 | Model |  | 2000GF
2 | Rated power | kW | 2000
3 | Rated rev. | rpm | 600
4 | Rated voltage | V | 11000
5 | Rated current | A | 131.2198
6 | Frequency | Hz | 50
7 | Power factor |  | 0.8 (lagging)
8 | Phase |  | 3-phase
9 | Voltage fluctuation rate | % | ±1
10 | Frequency (rev.) fluctuation rate | % | ±0.5
11 | Stable voltage regulating rate | % | ±2.5
12 | Stable frequency (rev.) regulating rate | % | 5
13 | Transient frequency (rev.) regulating rate | % | ±20～-15
14 | Stabilizing time | s | 5
15 | Voltage regulating method |  | Auto
16 | Speed Governor |  | Electrical hydraulic
17 | Frequency regulating method |  | Auto
18 | Lubricating method |  | Pressure lubricating
19 | Cooling method |  | Close circuit of fresh cooling water
20 | Coupling |  | Flexiable
21 | Painting color |  | Blue
22 | Overall dimension | mm | 9522x2736x3261
23 | Net weight | kg | 52550
Ⅱ. Diesel engine specification
No. | Item | Unit | Specification
1 | Engine Model |  | GA8300ZD30
2 | Type |  | In-line, 8-Cyls, four-stroke, direct injection, charged, inter cooled
3 | Bore | mm | 300
4 | Stroke | mm | 380
5 | Total displacemen | L | 214.64
6 | Mean piston seed | m/s | 7.6
7 | Rated power | KW | 2206
8 | Rated rev. | rpm | 600
9 | Overload (1 hr per 12 hrs) | kW/rpm | 2426/600
10 | Mean effective pressure | MPa | 2.05
11 | Compression ratio |  | 13
12 | Rotation direction |  | Clockwise, viewed from flywheel end.
13 | Firing order |  | 1-5-7-3-8-4-2-6
14 | Specific fuel oil consumption | g/kW.h | 198+3%
15 | Specific Lube oil consumption | g/kW.h | < 0.8
16 | Smoke | RB | ≤0.3
17 | Noise | dB(A) | 105
18 | Starting method |  | Air Rotary valve
19 | Cooling system |  | Fresh water cooling
20 | Lubricating system |  | Pressure lubricating
21 | Fuel oil specification |  | Diesel oil and 380Cst/50℃ HFO
22 | Lube oil specification |  | CD40 with TBN according HFO
23 | Piston lifting height | mm | 2600
24 | Overall dimension | mm | 5620×1620×2760mm
25 | Net weight | kg | 31000
Ⅲ. Alternator specification
No. | Item | Unit | Specification
1 | Alternator Model |  | FC 2000
2 | Type |  | Brushless generator
3 | Rated power | kW | 2000
4 | Rated voltage | V | 11000
5 | Rated current | A | 131.2198
6 | Frequency | Hz | 50
7 | Power factor |  | 0.8 (lagging)
8 | Working condition |  | Continuous
9 | Phase and connection |  | 3-phase, 6-wires
10 | Voltage regulation method |  | Brushless, self excited
11 | Insulation Class |  | F
12 | Protection Class |  | IP23
备注： Remark:
1. Rating for Gen-Set are based on the standard environment conditions: Ambient temperature: 25℃; Total barometric pressure: 100kPa; Charge air coolant temperature: 25℃; Relative humidity: 30% If the test ambient conditions are not same as the standard ambient conditions, the power and fuel consumptions should be revised according to ISO-3046.
2. The Gen-set is allowed to run continuously or intermittently with 110% rated power for 1 hour every 12 hours.

## Spare parts
Generator Standard Spare parts with engine
序号 | 代 号 | 名 称 | 数量 | 备 注
Item | Part Code | Part Name | Qty | Remark
1 | G-01-027 | 摇臂座螺栓 | 1
Bolt of rocker arm frame
2 | G-01-037 | 阀帽 | 2
Valve cap
3 | G-01-038 | 卡块 | 2副
|  | Valve collet | Sets
4 | 8G-A01-041 | 气阀外弹簧 | 4
Outer valve spring
5 | G-01-A042 | 进气阀 | 2
Intake valve
6 | G-01-043 | 气阀导管 | 4
Intake valve guide
7 | 8G-A01-047 | 气阀内弹簧 | 4
Inner valve spring
8 | G-A01-A072 | 排气阀 | 2
Exhaust valve
9 | G-01-207 | 顶架调节螺钉 | 2
Adjusting screw for valve pushed holder
10 | G-01-212 | 调节螺钉 | 1
Adjusting screw
11 | G-01-218A | 顶架硬块 | 2
Balance block
12 | GB/T 6171-86 | 螺母M24×2 | 1
|  | Nut |  | Used for adjusting valve lash
13 | GB/T 6173-86 | 螺母M18×1.5 | 1 | Used for adjusting
|  | Nut |  | valve pushed holde
14 | GN-03-003 | 气缸套封水圈 | 3
Water-seal ring for cylinder liner
15 | G-03-013C | 封水圈 | 30
Water-seal ring
16 | GN-03-015 | 气缸盖垫片 | 5
Cylinder head gasket
17 | GN-03-016 | 气缸套垫片 | 1
Cylinder liner copper-shim
18 | GN-03-033 | 凸轮轴承 (盖) | 1
Camshaft bearing (in cap)
19 | GN-03-034 | 凸轮轴承 (体) | 1
Camshaft bearing(in body)
20 | 8G-A04-003 | 轴瓦 | 4副 | Used for main bearing
|  | Bearing metal | Sets | and crank pin bearing
21 | G-04-034 | 止推片 | 1副
|  | Thrust ring | Sets
22 | G-04-088 | 顶高螺栓 | 8
Jacking bolt
23 | GA-05-002 | 第一道活塞环 | 1
No.1 Compression ring
24 | GA-05-003 | 第二道活塞环 | 1
No.2 Compression ring
25 | GA-05-004 | 第三道活塞环 | 1
No.3 Compression ring
26 | GA-05-100 | 螺旋撑簧油环 | 1 | 第 四道 活 塞 环
| GN-05-006 | Oil scraper ring |  | No.4 Compression ring
Generator Standard Spare parts with engine
27 | 8GN-10-033A | 排气管垫片 | 2
| 8GN-10-034A | Exhaust pipe gasket | 1
28 | G-10B-600 | 气缸盖排气口垫片组件 | 2
Gasket sub-assy for exhaust port of cylinder head
29 | 8G-B10-700 | 增压器进口垫片(组 件) | 2 | ≤2795kW机用(use)
Turbocharger inlet gasket sub-assy
30 | 8GN-10-400 | 脉冲转换器波纹管组件 | 2
Pulse Converter bellow
31 | 8GN-10-034A | 脉冲转换器垫片 | 4
Gasket
32 | 8GN-10-300 | 波纹管组件 | 1
Bellow
33 | 8G-B10-300 | 波纹管组件 | 1
Bellow
34 | G-36-008 | 垫圈 | 2
Washer
35 | 8GN-44-1600 | 高压油管组件 | 1
Injection pipe sub-assy
36 | G-45D-011 | 柱塞弹簧 | 2 | ≤2795Kw机用(use)
Plunger spring
37 | G-45D-600A | 柱塞偶件 | 2副 | ≤2795Kw机用(use)
|  | Plunger with barrel | Sets
38 | 16V32G-210100A | 出油阀偶件 | 2副 | ≤2795Kw机用(use)
|  | Delivery valve sub-assy | Sets
39 | G-46S-200 | 喷油嘴偶件 | 2副
|  | Injection nozzle sub-assy | Sets
40 | G-46-05 | 垫片 | 2
Washer
41 | G-46-09 | 垫片 | 2
Washer
42 | G-66-A200 | 安全阀组件 | 1
Safety valve assy
43 | GJG-01-702 | 大密封圈座 | 2
Big seal-ring seat
44 | GJG-01-703 | 大密封圈 | 2
Big seal ring
45 | GJG-01-705 | 密封圈 | 2
Seal ring
46 | GJG-01-706 | 密封圈座 | 2
Seal ring seat
47 | GJG-02-105 | 大密封圈 | 2
Big seal ring
48 | GJG-02-106 | O型密封圈 | 2
O-shape seal ring
49 | Q/NDJ66-95 | 垫圈 10 | 2
Washer
50 | Q/NDJ66-95 | 垫圈 24 | 5
Washer
51 | Q/NDJ66-95 | 垫圈 27 | 5
Washer
52 | Q/NDJ 301-95 | 球面管节 6 | 6
Spherical pipe joint
Generator Standard Spare parts with engine
53 | Q/NDJ302-95 | 螺母 M6 | 6
Connecting nut
54 | Q/NDJ305-95 | 单管接头 6 | 6
Mono siphonium joint
55 | Q/NDJ65-95 | 螺栓 M10 × 1 | 1
Hinged bolt
56 | Q/NDJ63-95 | 管接头体 6 | 1
Pipe joint body
57 | GB3452.1-92 | O型密封圈Φ47.5×3.55 | 6
O-rubber-seal ring
58 | 300-102A-02 | 温包插座 | 7
Temperature socket
59 | 300-102A-50 | 油压温包插座焊接组件 | 1
Pressure & temperature socket assy
60 | G-17B-000 | 起动阀部件 | 1套
|  | Starting valve assy | 1 Set
61 | G-32-000 | 盘车控制阀部件 | 1套 | 随机附件
|  | Barring control valve assy | 1 Set | Engine accessory
62 | G-67A-000A | 调压阀部件 | 1套 | 随机附件
|  | Adjusting pressure valve assy | 1 Set | Engine accessory
63 | G-69-000 | 高压空气滤清器部件 | 1套 | 随机附件
|  | High pressure air filter assy | 1 Set | Engine accessory
64 |  | 增压器备件箱 | 1
Spare parts case for turbocharger
65 | G-23-002 | 垫圈 | 2
Washer
66 | G-23-812 | 接头 | 2
Joint
67 | G-23-813 | 联接螺母 | 2
Connecting nut

## Tools and documents
Special tools 专用工具
序号 | 图 号 | 名 称 | 数量 | 备 注
Item | Part Code | Part Name | Qty | Remark
1 | GJG-01-100N | 装拆气门锁夹工具 | 1
Tool for mounting and dismantling valve collet
2 | GJG-01-210 | 手提研磨进排气阀工具 | 1
Manual lapping tool for intake and exhaust valve
3 | GJG-01-300N | 拆吊喷油器工具 | 1
Tool for dismantling fuel injector
4 | GJG-01-400 | 吊气缸盖工具 | 1
Lift tool for cylinder head
5 | GJG-01-600 | 气缸盖螺母扳手 | 1
Socket wrench for cylinder head nut
6 | GJG-01-700 | 气缸盖螺栓液压拉伸器 | 4
Hydraulic tension tool for cylinder head bolt
7 | GJG-02-100 | 贯穿螺栓拉伸器 | 2
Hydraulic tension tool for pull-rod bolt
8 | GJG-02-200 | 贯穿螺栓螺母扳手 | 1
Socket wrench for pull-rod nut
9 | GB/T 825-88 | 螺钉 M10 | 1
Screw
10 | GNJG-03-100 | 缸套拆装工具 | 1
Stripper for cylinder liner
11 | GNJG-04-100 | 拆主轴承盖工具 | 1
Stripper for main bearing cap
12 | GJG-04-201 | 主轴承螺母套筒 | 1
Socket wrench for main bearing nut
13 | GJG-04-300N | 飞轮端主轴承螺栓扳手 | 1
Socket for main bearing bolt of the flywheel end
14 | GNJG-05-100 | 装活塞工具 | 1
Tool for mounting piston
15 | GNJG-05-200 | 吊活塞工具 | 1
Lift tool for piston
16 | GJG-06-101A | 连杆螺母套筒 | 1
Socket wrench for connecting-rod nut
17 | GJG-06-102 | 扳棒 | 1
Wrench stick
18 | GJG-07-100N | 拆主轴瓦工具 | 1
Tool for dismantling main bearing metal
19 | GJG-07-200N | 拆主轴瓦工具 | 1
Tool for dismantling main bearing metal
20 | GJG-07-300 | 飞轮螺栓螺母扳手 | 1
Socket wrench for flywheel nut
21 | GB/T 825-88 | 螺钉 M36 | 1 | 吊飞轮用
|  | Screw |  | Lift for flywheel
22 | GJG-07-500 | 拆末端主轴瓦工具 | 1
Dismantling tool for main bearing metal of rear end
23 | GJG-07-600 | 不吊出活塞拆连杆轴瓦工具 | 1
Tool for dismantling connecting-rod bearing metal in case of that piston doesn’t need to be lifted
24 | GJG-07-700 | 曲轴后端齿轮螺母套筒扳手 | 1
Socket wrench for gear nut of crankshaft rear end
25 | GJG-07-800 | 飞轮螺母辅助扳手 | 1
Assistant wrench for flywheel nut
Special tools 专用工具
序号 | 图 号 | 名 称 | 数量 | 备 注
Item | Part Code | Part Name | Qty | Remark
26 | GJG-07-900 | 桥规工具 | 1 | 已有专用木箱
|  | Bridge gauge |  | Provided with special kit
27 | GJG-12-100 | SD-1型手动高压油泵 | 2
SD-1 manual high pressure pump
28 | GJG-12-300N | 拆装凸轮轴工具 | 2
Tool for mounting and dismantling camshaft
29 | G-60A-000 | 喷油器冷却器部件 | 1 | 3.2m²
Injector cooler assy
30 | GJG-12-500N | 装凸轮液压工具 | 1
Hydraulic tool for mounting cam
31 | GJG-57-100 | 燃油泵顶柱调 整 螺 母 扳 手 | 1
Mooned wrench for adjusting nut of injection pump tappet
32 | GJG-57-200 | 燃油泵顶柱调整棒 | 1
Adjusting stick for injection pump tappet
33 | GJG-57-300 | 燃油泵顶柱撬棒 | 1
Prize for injection pump tappet
34 | GJG-B58A-000 | 水泵叶轮拆卸器 | 1
Stripper for water pump impeller
35 | G-08N-000 | 手动盘车装置部件 | 1 | 其中G-08-009在在随机附属设备箱内
Manual barring device
36 | G-88A-000 | 喷油器试验工具部件 | 1
Tester for fuel injection pressure
37 | GJG-07-1000 | 曲轴甩档(臂距差)表 | 1
Measuring gauge for crank webs deflection
Spare meters 备用仪表
序号 | 图 号 | 名 称 | 数量 | 备 注
Item | Part Code | Part Name | Qty | Remark
1 | G-39B-032 | 淡水压力表 | 1 | Y-60T(0-0.4MPa)
Fresh water pressure gauge
2 | G-39B-033 | 燃油、气缸盖滑油压力表 | 2 | Y-60T(0-0.6MPa)
Fuel oil pressure gauge & lube oil pressure gauge for cylinder head
3 | G-39B-034 | 滑油压力表 | 1 | Y-60T(0-1MPa)
Lube oil pressure gauge
4 |  | 气缸盖出水温度计 | 4 | WSS-75(0-100℃)
Outlet water thermometer for cylinder head
5 | G-39C-041 | 淡水温度表 | 1 | WTZ-288(0-100℃)
Fresh water thermometer
6 | G-39B-032 | 压力表 | 1 | Y-60T(0-0.4MPa)
|  | Pressure gauge |  | For injector cooling oil
Documents 随机文件
| 序号 | 名 称 | 数量 | 备注
| Item | Document Name | Qty | Remark
| 1 | 产品证明书 | 1
Product certificate
| 2 | GN320型柴油机零件图册 | 1
Part list with drawings for Model GN320 engine
| 3 | 调速器使用说明书 | 1
Operating manual for governor
| 4 | 增压器使用说明书 | 1
Operating manual for turbocharger
| 5 | 温度巡测仪说明书 | 1
Operating manual for temperature control detector
| 6 | 燃油滤清器说明书 | 1 | In engine attached
|  | Operating manual for fuel filter |  | device case
| 7 | 滑油滤清器说明书 | 1 | In engine attached
|  | Operating manual for lube oil filter |  | device case
| 8 | 增压空冷器说明书 | 1 | In engine attached
|  | Charge air cooler operation maintenance manual |  | device case
| 9 | GN320和300系列柴油机燃用重油使用手册 | 1 | With heavy fuel oil diesel engine
Operation manual with heavy fuel oil for series GN320 and 300 diesel engine.