## Quotation
TO：
Power Plant 5×2MW Equipment Quotation
No. | Equipment | Qty | Unit | Unit Price (USD) | Total Price (USD) | Remark
1 | 燃气发电机组 2000kW 11kV/50Hz Standard 2MW/11KV/50Hz generating set | 5 | sets
1.1 | 燃气发动机 GN8320 2206kW@600rpm Gas engine GN8320 2206kW@600rpm | 5 | sets
1.2 | 燃气发动机附属设备 Gas engine accessory equipments | 5 | sets
1.3 | 发电机 11kV 10P IP23 600rpm Three phase syn. brushless alternator | 5 | sets
1.4 | 机组高压开关柜 Gen-set Switchgear | 5 | sets |  |  | KYN28-12，带继保
1.5 | 机组集控台 Gen-set control board | 5 | sets
1.6 | 机组机旁台 Gen-set local control desk | 5 | sets
1.7 | 共同底座及联轴器 Common base frame and flexible coupling | 5 | sets
1.8 | 弹性安装减震块 Semi-block damper | 5 | sets
1.9 | 基础螺栓 Foundation Bolts | 5 | sets
2 | 电站机组外围机械设备 Power Plant Auxiliary Equipment | 5 | lot
2.1 | 排气消音器 Exhaust silencer | 5 | sets
2.2 | 膨胀节 Expansion joint | 5 | sets
2.3 | 排气管 Exhaust piping | 5 | sets
2.4 | 冷却塔 Cooling Tower | 5 | sets
2.5 | 高温水膨胀水箱 HT water expansion tank | 5 | sets
2.6 | 外置润滑油箱 2000L带阀门 External lubricating oil tanker | 5 | sets
2.7 | 管道旁通离心滤器 Bypass type centrifugal separator | 5 | sets
2.8 | 滑油液位指示器 Lubricating oil level indication | 5 | sets
2.9 | 电站移动润滑油泵 Power plant dolly LO pump | 2 | sets
2.1 | 电动空压机组 Electrical motor driven air compressor | 3 | sets
2.11 | 柴油机空压机组 Diesel engine driven air compressor | 1 | sets |  |  | 295燃气发动机带
2.12 | 压缩空气瓶 Compressed air receiver | 5 | sets
3 | 电站电气动力柜 Power Plant Electrical Panel | 1 | lot
3.1 | 11kV 电站母线压变柜 11kV Busbar PT panel | 1 | set
3.2 | 电站11kV总出线柜 630A VS1-12 Power Plant 11kV Main Outgoing panel | 4 | set
3.3 | 电站所用变出线柜 Power Plant aux. transformer panel | 1 | set
3.4 | 电站800kVA所用变 800kVA Station Transformer | 1 | set
3.5 | 电站低压总柜 （GCS柜） 400V LV Main Panel | 1 | set
3.6 | 电站低压柜 （GCS柜） 400V LV distribution Panel | 2 | set
3.7 | 电站直流电源 DC Power for power plant | 1 | set
3.8 | 电站检修动力箱 Power plant maintenance cabinet | 6 | sets
4 | 油处理设备 OIL Treatment Equipment | 1 | lot
4.1 | 滑油分离机 Lubricating oil purified separator | 2 | sets
4.1.1 | 手动分离机组 LO separator
4.1.2 | 分离机组控制箱 Separator set control box
4.2 | 软水模块 Water soften module | 1 | set
5 | 机械材料(仅包括连接供方提供设备之间互联所必须的机械安装材料，如管道、法兰、接头等） Mechanical installation materials（only include necessary installation materail e.g. pipes, flanges and joints etc. for connection among equipments provided by the supplier） | 5 | lot |  |  | 可以提供清单供客户自己采购
6 | 电气安装材料(仅包括连接供方提供电气设备安装材料，如电线电缆等，发电机出线电缆等） Electrical installation materials (only include necessary materail e.g. wires and cables etc. for connection among equipments provided by the supplier） | 5 | lot |  |  | 可以提供清单供客户自己采购
7 | 机组随机备件工具(标准供货） Gen-set Spare parts and special tools | 5 | lot
8 | 专用工具 Special tools | 3 | set
9 | 文件 Documents | 5 | lot
10 | 共计 Total
Notes
1. 所有报价基于Fob Ningbo.
All prices are based on Fob Ningbo port.
2. 提供交货后一年或累计运转2000小时质量保证，以先到为准。
Quality guaranty: Provide full warranty within one year or 2000 operating hours from the date of delivery which ever comes earlier applies.
3. 交货期：收到预付款后六个月内。
Date of delivery: 6 months after date of deposite.
4. 付款方式：30%预付款，70%交货前支付。
Payment: 30 percent advance payment, 70 before delivery.
5. 报价有效期为2023年2月28日前。
Valid date for the offer: before Feb. 28, 2023
6. 安装指导及调试
Installation guide and test
a.供方派遣2名工程师到现场指导安装和调试，为期约3个月。需方应支付供方工程师每人每天美元津贴。
The supplier will dispatch 2 engineers to guide installation and commissioning on site that will take about 3 months. The buyer shall pay an allowance of USD per day for one engineer during that period.
b.供方派遣2名工程师到现场培训和运行指导，为期约1个月。需方应支付供方工程师每人每天美元津贴。
The supplier will dispatch 2 engineers to train and guide operation on site that will take about 1 month. The buyer shall pay an allowance of USD per day for one engineer during that period.
c.供方工程师国内外往返机票、工作地的食宿、交通、医疗等由需方承担。
The home and abroad round trip ticket, lodging, food, traffice and medical treatment for the supplier engineers shall be borne by customer.

## Technical specification
Technical specificaiton for 2000GF1-3 Gen-sets
Ⅰ. Gen-set technical specification
No. | Item | Unit | Specification
1 | Model |  | 2000GF
2 | Rated power | kW | 2000
3 | Rated rev. | rpm | 600
4 | Rated voltage | V | 11000
5 | Rated current | A | 131.2
6 | Frequency | Hz | 50
7 | Power factor |  | 0.8 (lagging)
8 | Phase |  | 3-phase
9 | Voltage fluctuation rate | % | ±1
10 | Frequency (rev.) fluctuation rate | % | ±0.5
11 | Stable voltage regulating rate | % | ±2.5
12 | Stable frequency (rev.) regulating rate | % | 5
13 | Transient frequency (rev.) regulating rate | % | ±20～-15
14 | Stabilizing time | s | 5
15 | Voltage regulating method |  | Auto
16 | Speed Governor |  | Electrical hydraulic
17 | Frequency regulating method |  | Auto
18 | Lubricating method |  | Pressure lubricating
19 | Cooling method |  | Close circuit of fresh cooling water
20 | Coupling |  | Flexiable
21 | Painting color |  | Blue
22 | Overall dimension | mm | 8550x2663x3348
23 | Net weight | kg | 51000
Ⅱ. Diesel engine specification
No. | Item | Unit | Specification
1 | Engine Model |  | GN8320ZD
2 | Type |  | In-line, 8-Cyls, four-stroke, direct injection, charged, inter cooled
3 | Bore | mm | 320
4 | Stroke | mm | 380
5 | Total displacemen | L | 244.5
6 | Mean piston seed | m/s | 7.6
7 | Rated power | KW | 2206
8 | Rated rev. | rpm | 600
9 | Overload (1 hr per 12 hrs) | kW/rpm | 2426/600
10 | Mean effective pressure | MPa | 1.8
11 | Compression ratio |  | 13
12 | Rotation direction |  | Clockwise, viewed from flywheel end.
13 | Firing order |  | 1-5-7-3-8-4-2-6
14 | Specific fuel oil consumption | KJ/kW.h | ≤9000
15 | Specific Lube oil consumption | g/kW.h | < 0.8
16 | Smoke | RB | ≤0.3
17 | Noise | dB(A) | 105
18 | Starting method |  | Air Rotary valve
19 | Cooling system |  | Fresh water cooling
20 | Lubricating system |  | Pressure lubricating
21 | Fuel specification |  | Natural gas
22 | Lube oil specification |  | CD40 with TBN according NG
23 | Piston lifting height | mm | 2600
24 | Overall dimension | mm | 6175×1790×2940mm
25 | Net weight | kg | 27000
Ⅲ. Alternator specification
No. | Item | Unit | Specification
1 | Alternator Model |  | TF 2000
2 | Type |  | Brushless generator
3 | Rated power | kW | 2000
4 | Rated voltage | V | 11000
5 | Rated current | A | 131.2
6 | Frequency | Hz | 50
7 | Power factor |  | 0.8 (lagging)
8 | Working condition |  | Continuous
9 | Phase and connection |  | 3-phase, 6-wires
10 | Voltage regulation method |  | Brushless, self excited
11 | Insulation Class |  | F
12 | Protection Class |  | IP23
Remark:
1. Rating for marine genset are based on the standard environment conditions： Ambient temperature：45℃； Total barometric pressure：100kPa； Charge air coolant temperature：32℃； Relative humidity：30%。 If the test ambient conditions are not same as the standard ambient conditions, the power and fuel consumptions should be revised according to ISO-3046.
2. The Gen-set is allowed to run continuously or intermittently with 110% rated power for 1 hour every 12 hours.

## Spare parts
Generator Standard Spare parts with engine
序号 | 代 号 | 名 称 | 数量 | 备 注
Item | Part Code | Part Name | Qty | Remark
1 | G-01-027 | 摇臂座螺栓 | 1
Bolt of rocker arm frame
2 | G-01-037 | 阀帽 | 2
Valve cap
3 | G-01-038 | 卡块 | 2副
|  | Valve collet | Sets
4 | 8G-A01-041 | 气阀外弹簧 | 4
Outer valve spring
5 | G-01-A042 | 进气阀 | 2
Intake valve
6 | G-01-043 | 气阀导管 | 4
Intake valve guide
7 | 8G-A01-047 | 气阀内弹簧 | 4
Inner valve spring
8 | G-A01-A072 | 排气阀 | 2
Exhaust valve
9 | G-01-207 | 顶架调节螺钉 | 2
Adjusting screw for valve pushed holder
10 | G-01-212 | 调节螺钉 | 1
Adjusting screw
11 | G-01-218A | 顶架硬块 | 2
Balance block
12 | GB/T 6171-86 | 螺母M24×2 | 1
|  | Nut |  | Used for adjusting valve lash
13 | GB/T 6173-86 | 螺母M18×1.5 | 1 | Used for adjusting
|  | Nut |  | valve pushed holde
14 | GN-03-003 | 气缸套封水圈 | 3
Water-seal ring for cylinder liner
15 | G-03-013C | 封水圈 | 30
Water-seal ring
16 | GN-03-015 | 气缸盖垫片 | 5
Cylinder head gasket
17 | GN-03-016 | 气缸套垫片 | 1
Cylinder liner copper-shim
18 | GN-03-033 | 凸轮轴承 (盖) | 1
Camshaft bearing (in cap)
19 | GN-03-034 | 凸轮轴承 (体) | 1
Camshaft bearing(in body)
20 | 8G-A04-003 | 轴瓦 | 4副 | Used for main bearing
|  | Bearing metal | Sets | and crank pin bearing
21 | G-04-034 | 止推片 | 1副
|  | Thrust ring | Sets
22 | G-04-088 | 顶高螺栓 | 8
Jacking bolt
23 | GN-05-002 | 第一道活塞环 | 1
No.1 Compression ring
24 | GN-05-003 | 第二道活塞环 | 1
No.2 Compression ring
25 | GN-05-004 | 第三道活塞环 | 1
No.3 Compression ring
26 | GN-05-100 | 螺旋撑簧油环 | 1 | 第 四道 活 塞 环
| GN-05-006 | Oil scraper ring |  | No.4 Compression ring
Generator Standard Spare parts with engine
27 | 8GN-10-033A | 排气管垫片 | 2
| 8GN-10-034A | Exhaust pipe gasket | 1
28 | G-10B-600 | 气缸盖排气口垫片组件 | 2
Gasket sub-assy for exhaust port of cylinder head
29 | 8G-B10-700 | 增压器进口垫片(组 件) | 2 | ≤2795kW机用(use)
Turbocharger inlet gasket sub-assy
30 | 8GN-10-400 | 脉冲转换器波纹管组件 | 2
Pulse Converter bellow
31 | 8GN-10-034A | 脉冲转换器垫片 | 4
Gasket
32 | 8GN-10-300 | 波纹管组件 | 1
Bellow
33 | 8G-B10-300 | 波纹管组件 | 1
Bellow
34 | G-36-008 | 垫圈 | 2
Washer
35 | G-66-A200 | 安全阀组件 | 1
Safety valve assy
36 | GJG-01-702 | 大密封圈座 | 2
Big seal-ring seat
37 | GJG-01-703 | 大密封圈 | 2
Big seal ring
38 | GJG-01-705 | 密封圈 | 2
Seal ring
39 | GJG-01-706 | 密封圈座 | 2
Seal ring seat
40 | GJG-02-105 | 大密封圈 | 2
Big seal ring
41 | GJG-02-106 | O型密封圈 | 2
O-shape seal ring
42 | Q/NDJ66-95 | 垫圈 10 | 2
Washer
43 | Q/NDJ66-95 | 垫圈 24 | 5
Washer
44 | Q/NDJ66-95 | 垫圈 27 | 5
Washer
45 | Q/NDJ 301-95 | 球面管节 6 | 6
Spherical pipe joint
Generator Standard Spare parts with engine
1 | Q/NDJ302-95 | 螺母 M6 | 6
Connecting nut
2 | Q/NDJ305-95 | 单管接头 6 | 6
Mono siphonium joint
3 | Q/NDJ65-95 | 螺栓 M10 × 1 | 1
Hinged bolt
4 | Q/NDJ63-95 | 管接头体 6 | 1
Pipe joint body
5 | GB3452.1-92 | O型密封圈Φ47.5×3.55 | 6
O-rubber-seal ring
6 | 300-102A-02 | 温包插座 | 7
Temperature socket
7 | 300-102A-50 | 油压温包插座焊接组件 | 1
Pressure & temperature socket assy
8 | G-17B-000 | 起动阀部件 | 1套
|  | Starting valve assy | Set
9 | G-32-000 | 盘车控制阀部件 | 1套 | 随机附件
|  | Barring control valve assy | Set | Engine accessory
10 | G-67A-000A | 调压阀部件 | 1套 | 随机附件
|  | Adjusting pressure valve assy | Set | Engine accessory
11 | G-69-000 | 高压空气滤清器部件 | 1套 | 随机附件
|  | High pressure air filter assy | Set | Engine accessory
12 |  | 增压器备件箱 | 1
Spare parts case for turbocharger
13 | G-23-002 | 垫圈 | 2
Washer
14 | G-23-812 | 接头 | 2
Joint
15 | G-23-813 | 联接螺母 | 2
Connecting nut

## Special tools
Special tools 专用工具
序号 | 图 号 | 名 称 | 数量 | 备 注
Item | Part Code | Part Name | Qty | Remark
1 | GJG-01-100N | 装拆气门锁夹工具 | 1
Tool for mounting and dismantling valve collet
2 | GJG-01-210 | 手提研磨进排气阀工具 | 1
Manual lapping tool for intake and exhaust valve
3 | GJG-01-300N | 拆吊喷油器工具 | 1
Tool for dismantling fuel injector
4 | GJG-01-400 | 吊气缸盖工具 | 1
Lift tool for cylinder head
5 | GJG-01-600 | 气缸盖螺母扳手 | 1
Socket wrench for cylinder head nut
6 | GJG-01-700 | 气缸盖螺栓液压拉伸器 | 4
Hydraulic tension tool for cylinder head bolt
7 | GJG-02-100 | 贯穿螺栓拉伸器 | 2
Hydraulic tension tool for pull-rod bolt
8 | GJG-02-200 | 贯穿螺栓螺母扳手 | 1
Socket wrench for pull-rod nut
9 | GB/T 825-88 | 螺钉 M10 | 1
Screw
10 | GNJG-03-100 | 缸套拆装工具 | 1
Stripper for cylinder liner
11 | GNJG-04-100 | 拆主轴承盖工具 | 1
Stripper for main bearing cap
12 | GJG-04-201 | 主轴承螺母套筒 | 1
Socket wrench for main bearing nut
13 | GJG-04-300N | 飞轮端主轴承螺栓扳手 | 1
Socket for main bearing bolt of the flywheel end
14 | GNJG-05-100 | 装活塞工具 | 1
Tool for mounting piston
15 | GNJG-05-200 | 吊活塞工具 | 1
Lift tool for piston
16 | GJG-06-101A | 连杆螺母套筒 | 1
Socket wrench for connecting-rod nut
17 | GJG-06-102 | 扳棒 | 1
Wrench stick
18 | GJG-07-100N | 拆主轴瓦工具 | 1
Tool for dismantling main bearing metal
19 | GJG-07-200N | 拆主轴瓦工具 | 1
Tool for dismantling main bearing metal
20 | GJG-07-300 | 飞轮螺栓螺母扳手 | 1
Socket wrench for flywheel nut
21 | GB/T 825-88 | 螺钉 M36 | 1 | 吊飞轮用
|  | Screw |  | Lift for flywheel
22 | GJG-07-500 | 拆末端主轴瓦工具 | 1
Dismantling tool for main bearing metal of rear end
23 | GJG-07-600 | 不吊出活塞拆连杆轴瓦工具 | 1
Tool for dismantling connecting-rod bearing metal in case of that piston doesn’t need to be lifted
24 | GJG-07-700 | 曲轴后端齿轮螺母套筒扳手 | 1
Socket wrench for gear nut of crankshaft rear end
25 | GJG-07-800 | 飞轮螺母辅助扳手 | 1
Assistant wrench for flywheel nut
Special tools 专用工具
序号 | 图 号 | 名 称 | 数量 | 备 注
Item | Part Code | Part Name | Qty | Remark
26 | GJG-07-900 | 桥规工具 | 1 | 已有专用木箱
|  | Bridge gauge |  | Provided with special kit
27 | GJG-12-100 | SD-1型手动高压油泵 | 2
SD-1 manual high pressure pump
28 | GJG-12-300N | 拆装凸轮轴工具 | 2
Tool for mounting and dismantling camshaft
29 | GJG-12-500N | 装凸轮液压工具 | 1
Hydraulic tool for mounting cam
30 | GJG-B58A-000 | 水泵叶轮拆卸器 | 1
Stripper for water pump impeller
31 | G-08N-000 | 手动盘车装置部件 | 1 | 其中G-08-009在在随机附属设备箱内
Manual barring device
32 | GJG-07-1000 | 曲轴甩档(臂距差)表 | 1
Measuring gauge for crank webs deflection
Spare meters 备用仪表
序号 | 图 号 | 名 称 | 数量 | 备 注
Item | Part Code | Part Name | Qty | Remark
1 | G-39B-032 | 淡水压力表 | 1 | Y-60T(0-0.4MPa)
Fresh water pressure gauge
2 | G-39B-033 | 燃油、气缸盖滑油压力表 | 2 | Y-60T(0-0.6MPa)
Fuel oil pressure gauge & lube oil pressure gauge for cylinder head
3 | G-39B-034 | 滑油压力表 | 1 | Y-60T(0-1MPa)
Lube oil pressure gauge
4 |  | 气缸盖出水温度计 | 4 | WSS- 75(0-100℃)
Outlet water thermometer for cylinder head
5 | G-39C-041 | 淡水温度表 | 1 | WTZ-288(0-100℃)
Fresh water thermometer
6 | G-39B-032 | 压力表 | 1 | Y-60T(0-0.4MPa)
|  | Pressure gauge |  | For injector cooling oil
Documents 随机文件
| 序号 | 名 称 | 数量 | 备注
| Item | Document Name | Qty | Remark
| 1 | 产品证明书 | 1
Product certificate
| 2 | GN320型柴油机零件图册 | 1
Part list with drawings for Model GN320 engine
| 3 | 调速器使用说明书 | 1
Operating manual for governor
| 4 | 增压器使用说明书 | 1
Operating manual for turbocharger
| 5 | 温度巡测仪说明书 | 1
Operating manual for temperature control detector
| 6 | 滑油滤清器说明书 | 1 | In engine attached
|  | Operating manual for lube oil filter |  | device case
| 7 | 增压空冷器说明书 | 1 | In engine attached
|  | Charge air cooler operation maintenance manual |  | device case