## 4X8.73MW Quotation
Date:20221219 |  |  |  |  | Ref.No.: 20221219IRQ-B
Offer for 4×8.7MW 11kV 50Hz HFO power plant
No. | Item | Qty | Unit | Unit price(USD) | Total price(USD) | Remark
A | MAN 8730KW/11KV/50HZ generating set 发电机组MAN 8730KW/11KV/50HZ | 4 | sets |  |  | New,made in 2010
A-1 | Diesel engine 柴油机 | 4 | sets |  |  | Include
A-2 | Alternator 发电机 | 4 | sets |  |  | Include
A-3 | Base frame 共同底座 | 4 | sets |  |  | Include
A-4 | Flexible coupling 联轴器 | 4 | pcs |  |  | Include
A-5 | Turbocharger 涡轮增压器 | 8 | sets |  |  | Include
A-6 | Flexible connections 柔性连接件 | 4 | lots |  |  | Include
A-7 | Maintenance platform 发动机维护平台 | 4 | sets |  |  | Include
A-8 | Engine/generator control cabinet 发动机/发电机控制柜 | 4 | sets |  |  | include
B | Fuel oil system 燃油系统 | 1 | lot
B-1 | HFO unloading pump station 59m³/h 重油卸油泵站59m³/h | 1 | set
B-2 | DO unloading pump station 29m³/h 轻油卸油泵站 29m³/h | 1 | set
B-3 | HFO purifier separator Unit 重油净化分离单元 | 1 | set |  |  | SJ60,1 use 1 standby
B-4 | HFO Booster Unit 重油增压单元 | 1 | sets
B-5 | HFO supply unit 重油供油单元 | 1 | set
C | Oil tank system 油罐系统
C-1 | HFO Oil tank:600m³ 重油油罐600m³ | 4 | sets |  |  | Semi finished products, welded by the Owner on site
C-2 | HFO buffer tank 200m³ 重油缓冲油罐200m³ | 2 | sets |  |  | Semi finished products, welded by the Owner on site
C-3 | HFO daily tank 100m ³ 重油日用油罐100m³ | 1 | set |  |  | Semi finished products, welded by the Owner on site
C-4 | Diesel oil tank 200m ³ 柴油储罐200m³ | 1 | sets |  |  | Semi finished products, welded by the Owner on site
C-5 | Oil tank 20m³ 柴油机日用油罐20m³ | 2 | sets |  |  | Finished products, container transportation
C-6 | Sludge oil tank 20m³ 渣油罐 20m³ | 1 | set |  |  | Finished products, container transportation
C-7 | Oil water separation tank 油水分离槽 | 1 | set |  |  | Concrete structure, the owner is responsible for
D | Lubricating oil system unit 滑油系统 | 2 | sets
D-1 | Lubricating oil purifier separator Unit 滑油分离单元 | 2 | sets
D-3 | Lubricating supply oil unit 滑油输送单元 | 2 | sets
D-2 | Lubricating oil filling unit 滑油转运单元 | 1 | set
E | Compressed air system unit 压缩空气系统
E-1 | Starting air compressor unit(Motor driven) 启动空压机（电驱动） | 3 | sets
E-2 | Starting air compressor unit(Diesel engine driven) 启动空压机（柴油机驱动） | 1 | set
E-3 | Control air compressor unit 仪表用空压机 | 2 | set
E-4 | Air Receiver unit 空气瓶 | 4 | sets
E-5 | Control Air Receiver 仪用压缩空气罐 | 4 | sets
E-6 | 冷干机、过滤器、减压阀 | 4 | sets
F | Cooling system unit 冷却系统 | 4 | sets
F-1 | Radiator 散热器 | 4 | sets
F-2 | Low Cooling water pump 低温水冷却泵 | 4 | sets
F-3 | Water soften device 软水装置 | 1 | set |  |  | 10m³/h
G | Exhaust gas and transfer oil system 排气和导热油系统
G-1 | Exhaust gas silencer 排气消音器 | 4 | sets
G-2 | Expansion bellow 膨胀节 | 4 | sets
G-3 | Heat transfer oil boiler 1400kg/10bar 导热油锅炉1400kg/10bar | 2 | set
G-4 | Heat transfer oil 导热油 | 18 | m³
H | Intake air system 进气系统
H-1 | Air intake filter 进气滤器 | 4 | sets
I | 11kV Eectrical system 11KV电气系统
I-1 | 11kV 电站母线压变柜 11kV Busbar PT panel | 1 | set
I-2 | 电站11kV总出线柜 1250A VS1-12 Power Plant 11kV Main Outgoing Panel | 2 | sets
I-3 | Station transformer panel KYN28A-12 所用变柜 | 1 | set
I-4 | 机组高压开关柜 Gen-set Switchgear | 4 | sets
I-5 | 机组集控台 Gen-set control board | 4 | sets
I-6 | 机组机旁台 Gen-set local control desk | 4 | sets
K | 400V Eectrical system 400V电气系统
K-1 | Plant transformer (1250KVA 11KV//0.4KV) 站用变压器 (1250KVA 11KV//0.4KV) | 1 | set |  |  | S11-M
K-2 | 400 Volt main panel 低压总柜 | 1 | set
K-3 | 电站低压柜 （GCS柜） 400V LV distribution Panel | 4 | sets
L | Power Plant control 电站控制系统
L-1 | Air compressor control box 空压机动力箱 | 4 | sets
L-2 | Gen-set Aux. Control Panel 机组辅助控制箱 | 4 | sets
L-3 | Power plant aux. panel 电站辅助动力柜 | 4 | sets
L-4 | Separator power box 分离机房动力箱 | 1 | set
L-5 | 400 Volt supply panel for fuel station 油库动力箱 | 1 | set
M | DC System 直流屏系统
M-1 | DC control panel 直流控制柜 | 1 | set
M-2 | Battery panel 电池 | 1 | set |  |  | Include
R | Installation material 安装材料
R1-8 | Mechanical installation materials 机械安装材料 | 4 | sets
R9-15 | Electrical installation materials 电气安装材料 | 4 | sets
S | Spare parts and Documents 文件和随机备件 | 2 | sets
T | Special tools 专用工具 | 1 | set
Sub-total 小计
Notes:
1. All prices base on FOB Ningbo\Shanghai\ Qingdao port .
2.Quality guaranty: No warranty is provided for the generator set in stock. and other new products:Provide full warranty within one year from the date of delivery or 2000 operating hours, whichever comes first.
3.Date of delivery: 6 months after receipt of advance payment.
4. Payment: 30 percent advance payment, 70 percent before shipment.
5. Valid date for the offer: before Mar. 30, 2023
6. The offer is for equioment inside the power plant only. All civil work and fuel tanks should be taken out by customer.
7. Installation guide and test:
a.The costs for traveling between China and customer,28day medical and isolation. lodging and food shall be borne by customer.
b. USD 200 salary per day for one engineer (total 2-4 persons) during installation supervision and test (about 2-3 months).
8. Factory building, foundation, road, civil construction, crane, lighting, fire fighting, contact expenses borne by the buyer.

## Technical specification
Technical specificaiton for Power plant equipments
Ⅰ. Gen-set technical specification
Item | Equipment | Unit | Specification
1 | Model |  | 8730GF
2 | Rated power | kW | 8730
3 | Rated rev. | rpm | 750
4 | Rated voltage | V | 11000
5 | Rated current | A | 572.7745
6 | Frequency | Hz | 50Hz
7 | Power factor |  | 0.8 (lagging)
8 | Phase |  | 3-phase
9 | Voltage fluctuation rate | % | ±1
10 | Frequency (rev.) fluctuation rate | % | ±0.5
11 | Stable voltage regulating rate | % | ±2.5
12 | Stable frequency (rev.) regulating rate | % | 5
13 | Transient frequency (rev.) regulating rate | % | ±20～-15
14 | Stabilizing time | s | 5
15 | Voltage regulating method |  | Auto
16 | Speed Governor |  | Electronic hydraulic
17 | Frequency regulating method |  | Auto/Manual
18 | Lubricating method |  | Pressure lubricating
19 | Cooling method |  | Close circuit of fresh cooling water
20 | Coupling |  | Flexiable
21 | Painting color |  | Munsel
22 | Overall dimension | mm | 12750x3730x5240
23 | Net weight | kg | 139000
Ⅱ. Diesel engine specification
No. | Item | Unit | Specification
1 | Engine Model |  | CMP-MAN 18V32/40
2 | Type |  | V32/40, 18-Cyls, four-stroke, direct injection, charged, inter cooled
3 | Bore | mm | 320
4 | Stroke | mm | 400
5 | Total displacemen | L | 579.06‬
6 | Mean piston seed | m/s | 10
7 | Rated power | kW | 9000
8 | Rated rev. | rpm | 750
9 | Overload (1 hr per 12 hrs) | kW/rpm | 11000/750
10 | Mean effective pressure | MPa | 2.49
11 | Compression ratio |  | 19
12 | Rotation direction |  | Clockwise, viewed from flywheel end.
13 | Firing order
14 | Specific fuel oil consumption | g/kW.h | 187+3%
15 | Specific Lube oil consumption | g/kW.h | < 0.8g/kW.h
16 | Smoke | RB | ≤0.3
17 | Noise | dB(A) | 105
18 | Starting method |  | Air Rotary valve
19 | Cooling system |  | Fresh water cooling
20 | Lubricating system |  | Pressure lubricating
21 | Fuel oil specification |  | Diesel oil and 380Cst/50℃ HFO
22 | Lube oil specification |  | CD40 with TBN according HFO
23 | Piston lifting height | mm | 2400
24 | Overall dimension | mm | 8995×3730×4420
25 | Net weight | kg | 85000
Ⅲ. Alternator specification
No. | Item | Unit | Specification
1 | Alternator Model |  | TFC / ZFC 8730
2 | Type |  | Brushless generator
3 | Rated power | kW | 8730
4 | Rated voltage | V | 11000 | g
5 | Rated current | A | 572.7745
6 | Frequency | Hz | 50
7 | Power factor |  | 0.8 (lagging)
8 | Working condition |  | Continuous
9 | Phase and connection |  | 3-phase
10 | Voltage regulation method |  | Brushless, self excited
11 | Insulation Class |  | F
12 | Protection Class |  | IP23
Remark:
1. Rating for genset are based on the standard environment conditions： Ambient temperature：25℃； Total barometric pressure：100kPa； Charge air coolant temperature：25℃； Relative humidity：30%。 If the test ambient conditions are not same as the standard ambient conditions, the power and fuel consumptions should be revised according to ISO-3046.
2. The Gen-set is allowed to run continuously or intermittently with 110% rated power for 1 hour every 12 hours.

## Spare parts
Spare parts and Documents 文件和随机备件
序号 | 名称 | 数量 | 图册号 | 备注
NO. | Part Name | Qty | Item | Note
曲轴和轴瓦/Crankshaft and bearing
1 | 上轴瓦 | 1 | 021.06.001 | 用于主轴承
| Bearing shell (upper) |  |  | For main bearing
2 | 下轴瓦 | 1 | 021.06.003 | 用于主轴承
| Bearing shell (lower) |  |  | For main bearing
3 | 主轴承螺栓 | 2 | 012.19.A13
Tie rod
4 | 主轴承螺母 | 2 | 012.19.A16
Nut
5 | 拉杆 | 2 | 012.19.A22 | 用于主轴承
| Stud |  |  | For main bearing
6 | 螺母 | 2 | 012.19.A25 | 用于主轴承
| Nut |  |  | For main bearing
7 | 止推片 | 2 | 021.06.008
Locating bearing ring
8 | 定距块 | 1 | 021.06.009
Stop piece
连杆和活塞/Connecting rod and main piston
9 | 连杆上轴瓦 | 1 | 030.02.A | 用于连杆
| upper bearing shell |  |  | For connecting rod
10 | 连杆下轴瓦 | 1 | 030.02.B | 用于连杆
| lower bearing shell |  |  | For connecting rod
11 | 连杆螺栓 | 2 | 030.02.016
Connecting rod bolt
12 | 螺母 | 2 | 030.02.017 | 用于连杆
| Nut |  |  | For connecting rod
13 | 连杆总成 | 1 | 030.02.K
Connecting rod, complete
14 | 活塞销衬套 | 1 | 030.02.A02
Piston pin bush
15 | 活塞销 | 1 | 034.12.001
Piston pin
16 | 挡圈 | 2 | 034.12.002
Retaining ring
17 | 活塞大总成（包括以下） | 1
Piston big complete (including the following parts)
17.1 | 活塞总成 | 1 | 34.12
Piston complete
17.2 | 活塞环（气环） | 1 | 034.15.001
Compression ring
17.3 | 活塞环（气环） | 1 | 034.15.002
Compression ring
17.4 | 活塞环（油环） | 1 | 034.15.004
Oil control ring
18 | 活塞环（气环） | 1 | 034.15.001
Compression ring
19 | 活塞环（气环） | 1 | 034.15.002
Compression ring
20 | 活塞环（油环） | 1 | 034.15.004
Oil control ring
气缸套和气缸盖/Cylinder liner and cylinder head
21 | 气缸套总成 | 1 | 050.07.001
Cylinder Liner
22 | O形圈 | 4 | 050.07.007
O--ring seal
23 | 火焰圈 | 1 | 050.07.029
Top land ring
24 | 气缸垫片 | 1 | 050.07.34
Sealing ring
25 | 气缸盖大总成（包括以下） | 1
Cylinder head, big complete (including the following parts)
25.1 | 气缸盖总成 | 1 | 055.10.K
Cylinder head complete
25.2 | 喷油器总成 | 1 | 221.04.K
Fuel injection valve, complete
25.3 | 进气阀总成 | 2 | 113.04.K
Inlet valve, complete
25.4 | 排气阀总成 | 2 | 114.03.K
Exhaust valve, complete
25.5 | 摇臂及其支架 | 1 | 111.04
Rocker arm with support
25.6 | 示功阀 | 1 | 419.04
Indicator valve
25.7 | 起动阀 | 1 | 161.02
Starting valve
25.8 | 安全阀 | 1 | 57.03
Safety valve
26 | 气缸盖螺栓 | 2 | 012.19.012
Tie rod
27 | 螺母 | 2 | 012.19.016
Nut
28 | 衬环 | 2 | 012.19.014
Ring
29 | O形圈 | 4 | 012.19.015
O--ring seal
30 | 衬环 | 2 | 012.19.A15
Ring
31 | O形圈 | 4 | 012.19.A14
O--ring seal
32 | 衬环 | 2 | 012.19.A23
Ring
33 | O形圈 | 4 | 012.19.A24
O--ring seal
气缸盖中的阀/Valves in cylinder head
34 | 起动阀 | 1 | 161.02.001
Starting valve
35 | 进气阀 | 2 | 113.04.001
Inlet valve cone
36 | 气阀导管 | 4 | 055.10.050
Valve guide
37 | 进气阀座 | 2 | 055.10.28
Inlet valve seat ring
38 | 排气阀 | 2 | 114.03.001
Exhaust valve cone
39 | 排气阀座 | 2 | 055.10.031
Outlet valve seat ring
40 | 安全阀 | 1 | 057.03.001
Safety valve
41 | 喷油器总成 | 5 | 221.04.K
Fuel injection valve, complete
高压油泵和高压油管/Fuel inection
42 | 燃油喷油泵 | 1 | 200.08.K
Fuel injection pump, complete
43 | 高压油管总成 | 1 | 434.17.K
Fuel injection pipe, complete
其它/Others
44 | O形圈 | 2 | 055.10.032
O-ring
45 | O形圈 | 6 | 055.10.070
O-ring
46 | O形圈 | 1 | 055.10.087
O-ring
47 | O形圈 | 5 | 055.10.051
O-ring
48 | O形圈 | 1 | 055.07.024
O-ring
49 | O形圈 | 2 | 055.10.040
O-ring
50 | O形圈 | 5 | 055.10.015
O-ring
51 | 垫片 | 1 | 055.10.086
Sealing ring
52 | 垫片 | 1 | 057.03.004
Sealing ring
53 | 垫片 | 1 | 050.07.C05
Sealing ring
54 | 垫片 | 1 | 050.07.C03
Sealing ring
55 | 增压器标准备件包 | 1
Standard spare part kit for T/C

## Special tools
Special tools 专用工具
序号 | 名称 | 数量 | 图册号
No. | Name | Qty | Item
1 | 连杆轴承拆装工具 | 1 | 30.249
Fit and removing device for connecting rod bearing
2 | 活塞连杆支撑工具 | 1 | 30.516
Supporting device
3 | 轴颈油道密封装置 | 1 | 20.05
Blocking tool
4 | 主轴承盖拆装工具 | 1 | 21.336
Lifting/lowering device for main bearing cap
5 | 主轴瓦拆卸工具 | 1 | 021.265/021.268/021.226
Dismantling tool for main bearing shell
6 | 定距管 | 2 | 50.133
Spacer pipe
7 | 高压油管拆装工具 | 1 | 001.766/009.088/434.041
Fitting/unfitting tools for high pressure pipe
8 | 气缸盖起吊工具 | 1 | 55.205
Lifting device for cylinder head
9 | 喷油器及启动阀座研磨工具 | 1 | 55.197
Grinding tool for fuel valve seat and starting valve seat
10 | 气缸盖清洁工具 | 1 | 55.149
Cleaning tool for cylinder head
11 | 气缸套及冷却水套拆装工具 | 1 | 50.099
Lifting device for cylinder liner
12 | 气缸套拆装工具 | 1 | 50.129
Fitting/unfitting tool for cylinder liner
13 | 火焰圈拆卸工具 | 1 | 50.165
Fitting/unfitting tool for flame ring
14 | 活塞吊装工具 | 1 | 34.142
Lifting device for piston
15 | 活塞安装导向圈 | 1 | 34.1
Guide bush for piston
16 | 起动阀拆装工具 | 1 | 161.018
Fitting/unfitting tool for starting vavle
17 | 手动调节杆 | 1 | 203.008
Lever
18 | 喷油泵升程测量工具 | 1 | 200.097
Measuring device for rise range for fuel pump
19 | 气阀弹簧拆装工具 | 1 | 113.211
Valve spring tensioner
20 | 气阀间隙调整工具 | 1 | 113.226
Setting tool for valve clearance
21 | 定位工具 | 1 | 113.227
Locating device
22 | 阀座拉拔工具 | 1 | 113.218
Extractor for valves
23 | 气阀导管拆装及阀座安装工具 | 1 | 113.219
Fitting/unfitting tool for valve seat and guide
24 | 喷油器拆装工具 | 1 | 221.181/221.182
Fitting/unfitting tool for fuel valve
25 | 喷油嘴夹紧工具 | 1 | 221.21
Tightening device for nozzle
26 | 喷油泵弹簧拆装工具 | 1 | 200.074
Fitting/unfitting tool for fuel pump spring
27 | 锁夹 | 1 | 200.078
Clamp with
28 | 喷油泵吊装工具 | 1 | 200.079
Fitting/unfitting tool for fuel pump
29 | 喷油泵柱塞拆卸工具 | 1 | 200.109
Removing tool for fuel pump plug
30 | 示功阀扳手 | 1 | 419.011
Socket wrench
31 | 阀线对研工具 | 1 | 113.224
Touching up device
32 | 排气阀间隙测量塞尺(t=0.9) | 3 | 113.139
Setting gauge for inlet valve clearance
33 | 进气阀间隙测量塞尺(t=0.2) | 2 | 0.455
Setting gauge for exhaust valve clearance
34 | 套筒扳手 | 1 | 200.096
Hexagon screw driver
35 | 加长杆 | 1 | 200.073
Ring extension
36 | 连杆安装导向工具 | 1 | 30.246
Guide tube
37 | 输出端轴承拆装螺栓 | 1 | 21.264
Erection bolt
38 | 塞尺 | 1 | 0.454
Thickness gauges
39 | 导管 | 1 | 21.032
Guide tube
40 | 喷油器试验台 | 1
Nozzle test bed
41 | 液压拉伸工具 | 1套 | 980.05
| Hydraulic tools | 1set
42 | 增压空气管和旁通管密封装置 | 1 | 280.016/280.029/280.030
Cover for charge air pipe
43 | 连杆大端固定工具 | 1 | 30.245
Turning stirrup
44 | 通用工具 | 1套 | 980.08 (001~033)
| General tools | 1set
45 | 连杆大端拆装工具 | 1 | 30.275
Fit and removal device for con. rod bearing
46 | 套筒扳手 | 1 | 200.095
Hexagon screw driver
47 | 衬套弹簧拆卸工具 | 1 | 27.018
Removing tool bush spring
48 | 夹紧板 | 1 | 27.019
Clamp
49 | 甩档表 (机械式) | 1
Crankshaft alignment gauge (autolog)
50 | 柴油机（整机）起吊工具 | 1
Lifting tool for whole engine
51 | 爆压表（机械式） | 1
Max. pressure indicator
52 | 喷油器清理工具 | 1 | 2.701
Cleaning tool for fuel injector
53 | 塑料盒 | 1 | 2.706
Packing box
54 | 清洁针 | 1套 | 2.718
| Cleaning wire | 1set
55 | 吊环螺钉 | 1 | 1.412
Eye bolt
56 | 套筒 36X20 | 2 | 1.771
Socket wrench insert 36x20
57 | 加长杆 20X200 | 2 | 1.913
Extension piece 20x200
58 | 活塞环扩张钳 | 1 | 34.11
Piston ring expander
59 | 直嘴孔用挡圈钳 | 1 | 2.165
Pliers for retaining ring
60 | 手动铰刀 | 1 | 34.096
Tap
61 | 铰刀把手 | 1 | 34.097
Tap wrench
62 | 套筒 | 1 | 1.797
Socket wrench insert
63 | 加长杆 | 1 | 1.914
Extension
64 | 拨杆 | 36 | 0.262
Tommy bar
65 | 套筒 | 1 | 1.767
Socket wrench insert
66 | 球头内六角扳手 | 1 | 0.445
Angular screw driver
67 | 梅花扳手 | 1 | 0.224
Double--ended ring spanner
68 | 套筒 | 1 | 1.868
Insert
69 | 吊环螺钉 | 1 | 1.404
Eye bolt
70 | 缸套内径千分尺 | 1
Micrometer screw
71 | 测量工具 | 1 | 50.164
Measuring device
72 | 增压器标准工具包 | 1
Standard tools kit for T/C
73 | 涡轮水洗工具 | 1
Wet cleaning device for turbo side
74 | 压气机水洗工具 | 1
Wet cleaning device for compressor side