## Quotation
Ref.No.:20221111 UGA-C |  |  |  |  | Date:20221111
TO：
Offer for 10×4MW HFO power plant
Item | Equipment | Qty | Unit | Unit Price (USD) | Total Price (USD) | Remark
1 | Standard 4MW/11KV/60Hz generating set 重油发电机组 | 10 | sets
1.1 | Engine NL8340 4500kW@600rpm 中速发动机 | 10 | sets
1.2 | Diesel engine accessory equipments 柴油机附属设备 | 10 | lots
1.2.1 | Engine driven HT circulating water pump 机带高温循环水泵 | 10 | lots
1.2.2 | Engine driven LT circulating water pump 机带低温循环水泵 | 10 | lots
1.2.3 | Engine driven LO pump 机带润滑油泵 | 10 | lots
1.2.4 | Torsional vibration damper 扭震减振器 | 10 | lots
1.2.5 | Speed governor 调速器 | 10 | lots
1.2.6 | Turbocharger 增压器 | 10 | lots
1.2.7 | Air cooler 中冷器 | 10 | lots
1.2.8 | Fuel strainer 燃油滤清器 | 10 | lots
1.2.9 | Prelubricating LO pump 预润滑电动油泵 | 10 | lots
1.2.10 | Water thermostatic valve 水温控制阀 | 10 | lots
1.2.11 | HT Water Cooler 高温淡水冷却器 | 10 | lots
1.2.12 | Lubricating oil thermostatic valve 滑油控制阀 | 10 | lots
1.2.13 | Lubricating oil Cooler 润滑油冷却器 | 10 | lots
1.2.14 | Local control desk 机旁仪表控制台 | 10 | lots
1.2.15 | Lubricating oil filter 滑油滤清器 | 10 | lots
1.2.16 | Lubricating oil pressure control valve 滑油压力控制阀 | 10 | lots
1.2.17 | Common base frame and flexible coupling 共同底座及联轴器 | 10 | sets
1.2.18 | Diesel Engine Driven Air Compressor 柴油空压机组 | 1 | sets
1.2.19 | Electrical motor driven air compressor 电动空压机组 | 4 | sets
1.2.20 | Compressed air receiver 压缩空气瓶 | 6 | sets
1.3 | Three phase syn. brushless alternator 发电机 11kV 12P IP23 600rpm | 10 | sets
1.4 | Gen-set Switchgear 机组高压开关柜 | 10 | sets |  |  | KYN28，带继保
1.5 | Gen-set control board 机组集控台 | 10 | sets
1.6 | Gen-set local control desk 机组机旁台 | 10 | sets
2 | Power Plant Auxiliary Equipment 电站机组外围机械设备 | 10 | lots
2.1 | Exhaust silencer 排气消音器 | 10 | pcs
2.2 | Expansion joint 膨胀节 | 10 | pcs
2.3 | Exhaust piping 排气管 | 10 | lots
2.4 | Radiator 散热器 | 10 | pcs
2.5 | HT water expansion tank 高温水膨胀水箱 | 10 | pcs
2.6 | Cooling Moduel 冷却模块 | 10 | pcs
2.7 | Bypass type centrifugal separator 管道旁通离心滤器 | 10 | pcs
2.8 | Lubricating oil level indication 滑油液位指示器 | 10 | sets
3 | Power Plant Electrical Panel 电站电气动力柜 | 1 | lot
3.1 | PT panel KYN28A-12 母线压变 | 1 | pc
3.2 | Power Plant 11kV Main Outgoing Panel 电站11kV总出线柜 | 5 | pcs
3.3 | Station transformer panel KYN28A-12 所用变柜 | 1 | pc |  |  | 1250A
3.4 | Linkage panel 联络柜 | 1 | pc
3.5 | Isolate panel 隔离柜 | 1 | pc
3.7 | Plant transformer (2000KVA/11/0.40) 所用变 | 1 | pc |  |  | S11
3.8 | Bus-bar 联络桥架 | 1 | set
3.9 | Station Batteries & Battery Charger with automatic float and boost control, indications and in built protections (220VDC/150Ah and 24VDC/150Ah supply panel) 直流屏 | 1 | pc
3.1 | 400Volt main panel 低压总柜 | 1 | pc |  |  | GCS
3.11 | 电站低压柜 （GCS柜） 400V LV distribution Panel | 6 | pcs
3.12 | Power plant aux. panel 电站辅助动力柜 | 9 | sets
3.13 | 400 Volt supply box for fuel station 油库动力箱 | 2 | sets
3.14 | Power plant maintenance control box 电站检修动力箱 | 20 | sets
3.15 | boiler control box 锅炉控制箱 | 4 | sets
3.16 | Duty oil pump control box 污油泵控制箱 | 1 | set
3.17 | Air compressor control box 空压机控制箱 | 6 | sets
4 | HFO Treatment Equipment 重油处理设备 | 1 | lot
4.1 | HFO purified separator module 重油分离机 | 2 | sets |  |  | SJ60
4.2 | Gen-set lubricating oil purified separator 润滑油分离机 | 3 | sets
4.3 | Fuel booster module 供油单元 | 2 | sets
4.4 | HFO unloading pump station 重油卸油泵站 | 1 | set
4.5 | DO unloading pump station 柴油卸油泵站 | 1 | set
4.6 | Heat transfer oil boiler 导热油锅炉 | 3 | sets
4.7 | Thermal oil 导热油 | 24 | m³
5 | Mechanical installation materials（only include necessary installation materail e.g. pipes, flanges and joints etc. for connection among equipments provided by the supplier） 机械材料(仅包括连接供方提供设备之间互联所必须的机械安装材料，如管道、法兰、接头等） | 10 | lot
6 | Electrical installation materials (only include necessary materail e.g. wires and cables etc. for connection among equipments provided by the supplier） 电气安装材料(仅包括连接供方提供电气设备安装材料，如电线电缆等，发电机出线电缆等） | 10 | lot
7 | Spare parts 随机备件工具 | 10 | lot
8 | Special tools 专用工具 | 2 | sets
9 | Documents 文件 | 10 | lot
10 | Oil tank system（17 days） 油罐系统(17天) | 1 | lot
Total Price（USD） 共计
1 | 土建工程 Civil works | 1 | lot |  |  | Owner's scope
2 | 钢结构厂房 Steel structure plant | 1 | lot |  |  | Owner's scope
3 | 照明系统 Lighting System | 1 | lot |  |  | Owner's scope
4 | 监控及安保系统 Monitoring and security system | 1 | lot |  |  | Owner's scope
5 | 避雷系统 Lightning protection system | 1 | lot |  |  | Owner's scope
6 | 消防系统 Fire fighting system | 1 | lot |  |  | Owner's scope
7 | 油罐现场安装 Field installation of oil tank | 1 | lot |  |  | Owner's scope
8 | 发电机组及附属设备现场安装工作 On site installation of generator set and auxiliary equipment | 1 | lot |  |  | Owner's scope
Notes
1. 所有报价基于FOB宁波港。
All prices are based on FOB NINGBO port.
2. 提供交货后一年或累计运转2000小时质量保证，以先到为准。
Quality guaranty: Provide full warranty within one year or 2000 operating hours from the date of delivery which ever comes earlier applies.
3. 交货期：收到预付款后8个月。
Date of delivery: 8 months after payment.
4. 付款方式：30%预付款，70%发货前支付。
Payment:30% advance payment, 70% before delivery.
5. 报价有效期为2022年12月30日前。
Valid date for the offer: before Dec. 30, 2022
6. 安装指导及调试
Installation guide and test
a.供方派遣6名工程师到现场指导安装和调试，为期约3个月。需方应支付供方工程师每人每天150美元津贴。
The supplier will dispatch 6 engineers to guide installation and commissioning on site that will take about 3 months. The buyer shall pay an allowance of USD 150 per day for one engineer during that period.
b.供方派遣2名工程师到现场培训和运行指导，为期约1个月。需方应支付供方工程师每人每天150美元津贴。
The supplier will dispatch 2 engineers to train and guide operation on site that will take about 1 month. The buyer shall pay an allowance of USD 150 per day for one engineer during that period.
c.供方工程师国内外往返机票、工作地的食宿、交通、医疗等由需方承担。
The home and abroad round trip ticket, lodging, food, traffice and medical treatment for the supplier's engineers shall be borne by customer.

## General technical specification
Technical specificaiton for Power plant equipments
Ⅰ. Gen-set technical specification
Item | Equipment | Unit | Specification
1 | Model |  | 4000GF
2 | Rated power | kW | 4000
3 | Rated rev. | rpm | 600
4 | Rated voltage | V | 11000
5 | Rated current | A | 262.4396
6 | Frequency | Hz | 60
7 | Power factor |  | 0.8 (lagging)
8 | Phase |  | 3-phase
9 | Voltage fluctuation rate | % | ±1
10 | Frequency (rev.) fluctuation rate | % | ±0.5
11 | Stable voltage regulating rate | % | ±2.5
12 | Stable frequency (rev.) regulating rate | % | 5
13 | Transient frequency (rev.) regulating rate | % | ±20～-15
14 | Stabilizing time | s | 5
15 | Voltage regulating method |  | Auto
16 | Speed Governor |  | Electronic hydraulic
17 | Frequency regulating method |  | Auto/Manual
18 | Lubricating method |  | Pressure lubricating
19 | Cooling method |  | Close circuit of fresh cooling water
20 | Coupling |  | Flexiable
21 | Painting color |  | Munsel
22 | Overall dimension | mm | 9790x2680x4650
23 | Net weight | kg | 82000
Ⅱ. Diesel engine specification
No. | Item | Unit | Specification
1 | Engine Model |  | NL8340ZD
2 | Type |  | In-line, 8-Cyls, four-stroke, direct injection, charged, inter cooled
3 | Bore | mm | 340
4 | Stroke | mm | 480
5 | Total displacemen | L | 348.6414
6 | Mean piston seed | m/s | 9
7 | Rated power | kW | 4500
8 | Rated rev. | rpm | 600
9 | Overload (1 hr per 12 hrs) | kW/rpm | 4950/600
10 | Mean effective pressure | MPa | 2.58
11 | Compression ratio |  | 19
12 | Rotation direction |  | Clockwise, viewed from flywheel end.
13 | Firing order |  | 1-4-7-6-8-5-2-3
14 | Specific fuel oil consumption | g/kW.h | 186+3%
15 | Specific Lube oil consumption | g/kW.h | < 0.8g/kW.h
16 | Smoke | RB | ≤0.3
17 | Noise | dB(A) | 105
18 | Starting method |  | Air Rotary valve
19 | Cooling system |  | Fresh water cooling
20 | Lubricating system |  | Pressure lubricating
21 | Fuel oil specification |  | Diesel oil and 180Cst/50℃ HFO
22 | Lube oil specification |  | CD40 with TBN according HFO
23 | Piston lifting height | mm | 2365
24 | Overall dimension | mm | 6830×2520×4000
25 | Net weight | kg | 47000
Ⅲ. Alternator specification
No. | Item | Unit | Specification
1 | Alternator Model |  | TFC / ZFC 4000
2 | Type |  | Brushless generator
3 | Rated power | kW | 4000
4 | Rated voltage | V | 11000
5 | Rated current | A | 262.4396
6 | Frequency | Hz | 60
7 | Power factor |  | 0.8 (lagging)
8 | Working condition |  | Continuous
9 | Phase and connection |  | 3-phase
10 | Voltage regulation method |  | Brushless, self excited
11 | Insulation Class |  | F
12 | Protection Class |  | IP23
Remark:
1. Rating for genset are based on the standard environment conditions： Ambient temperature：25℃； Total barometric pressure：100kPa； Charge air coolant temperature：25℃； Relative humidity：30%。 If the test ambient conditions are not same as the standard ambient conditions, the power and fuel consumptions should be revised according to ISO-3046.
2. The Gen-set is allowed to run continuously or intermittently with 110% rated power for 1 hour every 12 hours.

## Spare parts
Initial Spare parts
序号 | 代 号 | 名 称 | 数量 | 备 注
Item | Part Code | Part Name | Qty | Remark
1 | 330-01-025 | 密封垫 | 2
Seal ring
2 | 330-01-028 | 密封垫 | 2
Seal ring
3 | 330-01-038 | 卡 块 | 2副
|  | Valve collet | Sets
4 | 330-01-041 | 气 阀 外 弹 簧 | 4
Outer valve spring
5 | 330-01-042 | 进 气 阀 | 2
Intake valve
6 | 330-01-043 | 气 阀 导 管 | 4 | Intake & exhaust
|  | Intake valve guide |  | valve guides
7 | 330-01-047 | 气 阀 内 弹 簧 | 4
Inner valve spring
8 | 330-01-072 | 排 气 阀 | 2
Exhaust valve
9 | 330-01-205 | 压 球 座 | 1
Adjusting screw
10 | 330-01-207 | 顶 架 调 节 螺 钉 | 2
Adjusting screw for valve pushed holder
11 | 330-01-209 | 压 块 | 2
Valve cap
12 | 330-01-218 | 顶 架 硬 块 | 2
Balance block
13 | GB/T 6171-86 | 螺 母 M22×1.5 | 1 | Used for adjusting
|  | Nut |  | valve lash
14 | GB/T 6171-87 | 螺 母 M20×1.5 | 1 | Used for adjusting
|  | Nut |  | valve push holder
15 | GB/T 3452.1-92 | O型密封圈26.5×3.55G | 24
O- ring
16 | GB/T 3452.1-92 | O型密封圈28×3.56G | 24
O- ring
17 | GB/T 3452.1-92 | O型密封圈115×5.3G | 2
O- ring
18 | GB/T 3452.1-93 | O型密封圈437×7G | 2
O- ring
19 | 330-01-021 | 止推片 | 1
Thrust ring
20 | 340-01-036 | 气缸盖垫片 | 3
Cylinder head gasket
21 | 340-01-037 | 气缸盖垫片 | 3
Cylinder head gasket
22 | 330-01-039 | 轴瓦 | 2
| 330-01-041 | Bearing metal
23 | 340-03-047 | 汽缸套封水圈（下） | 2
Cylinder liner water sealing
24 | 340-03-049 | 汽缸套封水圈（下） | 1
Cylinder liner water sealing
25 | 330-03-051 | 凸轮轴轴承 | 1
Camshaft bush
26 | 330-03-052 | 自由端凸轮轴轴承 | 1
Free end camshaft bush
27 | 340-05-002 | 第一道活塞环 | 1
No.1 Compression ring
28 | 340-05-003 | 第二道活塞环 | 1
No.2 Compression ring
29 | 340-05-004 | 第三道活塞环 | 1
No.3 Compression ring
30 | 340-05-100 | 螺 旋 撑 簧 油 环 | 1
Oil scraper ring
31 | 330-06-003 | 连 杆 轴 瓦 | 2
Connecting rod bearing metal
32 | 330-10-100 | 排 气 管 垫 片 组 件 | 6
Exhaust pipe gasket sub-assy
33 | 330-10-600 | 气缸盖排气出口垫片组件 | 2
Cylinder head exhaust port gasket
34 | 340-10-700 | 增 压 器 进 口 垫 片 (组 件) | 2
Turbocharger inlet gasket sub-assy
35 | 330-17-000 | 起 动 阀 部 件 | 1set
Starting valve assy
36 | G-36-008 | 垫 圈 | 2
Washer
37 | 330-44-1600 | 高 压 油 管 组 件 | 1
Injection pipe sub-assy
38 | HP7400-200002 | 柱 塞 弹 簧 | 2
Plunger spring
39 | HP7100-200100 | 柱 塞 偶 件 | 2set
|  | Plunger with barrel | Sets
40 | 11.20005-0177-1.B | 出 油 阀 偶 件 | 2set
|  | Delivery valve sub-assy | Sets
41 | DN330-100200 | 喷 油 嘴 偶 件 | 2set
|  | Injection nozzle couple | Sets
42 | 330-66-000 | 安 全 阀 组 件 | 1set
|  | Safety valve assy | Set
43 |  | 增 压 器 备 件 箱 | 1
Spare parts case for turbocharger

## Tools and documents
Special tools 专用工具
序号 | 图 号 | 名 称 | 数量 | 备 注
Item | Part Code | Part Name | Qty | Remark
1 | 330JG-01-100 | 进 排 气 阀 装 拆 工 具 | 1
Tool for mounting and dismantling intake and exhaust valve
2 | 330JG-01-200 | 进 气 阀 研 磨 工 具 | 1
Lapping tool for intake valve
3 | 330JG-01-300 | 拆 吊 喷 油 器 工 具 | 1
Tool for dismantling fuel injector
4 | 330JG-01-400 | 吊 气 缸 盖 工 具 | 1
Lift tool for cylinder head
5 | 330JG-01-500 | 排 气 阀 研 磨 工 具 | 1
Lapping tool for exhaust valve
6 | 330JG-01-600 | 拆 装 水 封 套 管 工 具 | 1
Stripper for water
7 | 330JG-01-700 | 手柄组件（示功阀） | 1
Handle sub-assy(Indicator valve)
8 | 340JG-03-100 | 缸 套 拆 装 工 具 | 1
Stripper for cylinder liner
9 | 340JG-03-200 | 拆 火 焰 环 工 具 | 1
Stripper for cylinder liner ring
10 | 340JG-03-300 | 缸 套 装 入 工 具 | 1
Mounting for cylinder liner
11 | DNJG-03-210 | 拆 主 轴 承 盖 支 座 | 1
Bracket for main bearing cap
12 | DNJG-03-200 | 拆 主 轴 承 盖 工 具 | 1
Jack for main bearing nut
13 | 340JG-05-100 | 装 活 塞 工 具 | 1
Tool for mounting piston
14 | 340JG-05-200 | 吊 活 塞 工 具 | 1
Lift tool for piston
15 | 340JG-05-300 | 吊 活 塞 销 工 具 | 1
Lift tool for piston pin
16 | 330JG-06-100 | 连 杆 大 端 拆 装 工 具 | 1套
Stripper for the large end connecting rod bolt
17 | 330JG-07-100 | 拆 曲 轴 齿 轮 工 具 | 1
Dismantling tool for crankshaft gear
18 | DNJG-07-100 | 拆 主 轴 瓦 工 具 | 1
Dismantling tool for main bearing metal
19 | 330JG-12-001 | 导 向 筒 | 1
Hydraulic tool for mounting cam
20 | 330-88-000 | 喷 油 器 校 验 工 具 | 1
Tester for fuel injection pressure
21 | 330JG-95-100 | 侧 拉 螺 栓 拉 伸 器 | 1套
Hydraulic tension tool for side bolt
22 | 330JG-95-200 | 主 轴 承 螺 栓 拉 伸 器 | 1套
Hydraulic tension tool for main bearing bolt
23 | 330JG-95-300 | 气 缸 盖 螺 栓 拉 伸 器 | 1套
Hydraulic tension tool for cylinder head bolt
24 | 330JG-95-400 | 连 杆 螺 栓 拉 伸 器 | 1套 | with fasten hose
Hydraulic tension tool for connecting rod bolt
Documents
| 序号 | 名 称 | 数量 | 备注
| Item | Document Name | Qty | Remark
| 1 | DN8340 系 列 柴 油 机 使 用 说 明 书 | 1
Operating manual for series DN8330 diesel engine
| 2 | 产 品 证 明 书 | 1
Product certificate
| 3 | DN8340系 列 柴 油 机 零 件 图 册 | 1
Part list with drawings for series DN8430 engine
| 4 | 调 速 器 使 用 说 明 书 | 1
Operating manual for governor
| 5 | 增 压 器 使 用 说 明 书 | 1 | In spareparts kit for
|  | Operating manual for turbocharger |  | turbocharger
| 6 | 温 度 巡 测 仪 说 明 书 | 1
Operating manual for temperature control detector
| 7 | 燃 油 滤 清 器 说 明 书 | 1
Operating manual for fuel filter
| 8 | 滑 油 滤 清 器 说 明 书 | 1
Operating manual for lube oil filter
| 9 | 增 压 空 冷 器 说 明 书 | 1
Charge air cooler operation maintenance manual
| 10 | 发电机组使用说明书 | 1
Gen-set operation manual
| 11 | G300和300系列柴油机燃用重油使用手册 | 1
Operation manual with heavy fuel oil for series G300 and 300 diesel engine.

## Oil tank system
油罐材料报价（不含安装） Quotation of oil tank materials (excluding installation)
Item | Specifications | Dimensions | Qty | Unit Price | Total price | Weight | Remark
|  |  |  | USD | USD | KG
1 | 600m³重油罐 立式 600m³HFO tank (vertical) | Φ9000×10000 | 5 |  |  | 29559 | Thermal insulation
2 | 600m³柴油罐 立式 600m³DO tank (vertical) | Φ9000×10000 | 1 |  |  | 29000
3 | 200m³重油沉淀油罐 立式 200m³HFO buffer tank (vertical) | Φ6800×6000 | 3 |  |  | 15262 | Thermal insulation
4 | 100m³日用重油罐立式 100m³daily HFO tank (vertical) | Φ5200×5250 | 2 |  |  | 9498 | Thermal insulation
5 | 20m³日用柴油罐（卧式） 20m³ daily HFO tank（horizontal） | Φ2000×7000 | 3 |  |  |  | Floating ball pulley level gauge
6 | 20m³渣油罐（卧式） 20m³ Sludge tank (horizontal) | Φ2000×7000 | 1
7 | 国内运费 Domestic freight |  | 1
8 | 油罐区安装材料（机械+电气） Installation materials in oil tank farm (mechanical + Electrical) |  | 1
合计 Total Price
1 | 耗材 consumable material |  | 1 |  |  |  | Owner's scope
2 | 安装工具 Installation tools (welding, lifting) |  | 1 |  |  |  | Owner's scope
3 | 油漆 paint |  | 1 |  |  |  | Owner's scope
4 | 现场拼装焊接，除锈油漆工作等 On site assembly and welding, rust removal, painting, etc |  | 1 |  |  |  | Owner's scope
备注:1、报价中只含材料及预制制作费，末含防腐油漆及现场组装施工费。 Remarks:The quotation only includes the cost of materials and prefabrication, and does not include the cost of anti-corrosion paint and on-site assembly.