ANNEXURE- I

TECHNICAL SPECIFICATIONS, SCOPE, PERFORMANCE PARAMETERS, BATTERY LIMITS , EXCLUSIONS OF

2x 65  TPH 80 ATA, 515 +/- 5 Deg C,  Imported COAL FIRED BOILER

# 1.    SCOPE AND EXTENT OF SERVICES, TECHNICAL SPECIFICATIONS AND EQUIPMENT TO BE ERECTED ANd COMMISSIONED

### DESIGN BASIS

Type 		Atmospheric Fluidised 
		Bed Combustion

Steam Parameters:	Unit	
Maximum continuous rating (MCR) *	 TPH	65
Pressure at outlet of main steam stop 	Ata	80
valve and NRV
Temperature at superheater outlet	oC	515± 5
Temperature control range	% MCR	60-110
No of boilers	No	2

Feed water

Source                                                        Mixture of condensate and DM water

Temperature at inlet of deaerator	°C	27
(DM water + return condensate)

Temperature at inlet of	oC	102
economiser

Boiler shall be capable of operating with an output of 10% above the MCR for a period of 30 minutes, once in every 8 hours.  This “peaking” requirement should not affect the circulation ratio of the system.

Note :

*	The specified maximum continuous rating shall be the  gross output at main steam stop valve excluding any auxiliary steam requirement of the boiler.

- Vendor shall specify the quality of water required at the inlet of deaerator (DM water)

- DESIGN CRITERIA OF BOILER

### 2.1		Main Fuel

### Imported Coal

### 2.2        Firing Capability of Boiler on selected Fuels

As highlighted above, PURCHASER desires to burn Imported Coal, , the characteristics of which are given in clause 2.3.4.  Boiler shall, therefore, have burning capability on the selected fuels, at least, but not limited to that specified below:

| Fuel | Proportion on MCR % |
| --- | --- |
| Imported coal | 100 |

### 2.3	Feeding Arrangement

Fuel shall be fed as ‘underfeed’ during non-monsoon period. Supplier shall highlight the feeding system selected with justification.

Note :

Hence boiler shall be capable of burning Coal without any supporting fuel during under feed system which shall generally be adopted for feeding coal into the  boiler.

### 2.4		Typical Characteristics of Fuels

Typical characteristics of fuel proposed for the boilers are given below in detail

Imported  Coal

Carbon	%	30-50

Sulphur ADB	%	0.7-0. 9
Moisture(ARB)	%	10-20
Ash ADB	%	8-20

GCV	kcal/kg	5800- 6500

For the performance evaluation the GCV shall be 6300 Kcal/Kg.

# 3.0	ErectION and CommissionING ASISTANCE by the Vendor

The Vendor shall be responsible for the erection and commissioning of the Equipment supplied by them and all other items, which are part of the system. The Vendor shall be responsible for all aspects of the erection and commissioning of the 
2 x 65 tph power boiler.

Complete Design & Engineering of the Boiler & ESP including the items in Jubilant scope of work shall be in VENDOR Scope. VENDOR shall submit 3 sets of drawing for the review/ comments and shall submit 3 approved drawings for Construction along with soft copy.

- Boiler pressure parts consisting of

- Steam drum

- Furnace and headers

- Super heaters

- Attemperator

- Economiser

- Protection shields for first row of economizer top/bottom banks shall be provided with baffle plates for the bends.

- Mountings and fittings

- Fluidized bed combustion system of underfeeding systems

- Coal  bunker  of 24 hrs storage capacity   hopper with 2 mm SS lining for conical portion. Top chequered plate and cross beams to support the conveyors above .

- Rod gate damper below all bunkers

- Solid fuel firing equipment

- Feed Chutes at inlet of Fuel feeders

- Fuel Feeders

- Fuel Feeder discharge chutes

- Dedicated VFDs for Fuel Feeders

- Start-up fuel system

- Fuel oil tank  of Suitable Capacity

- Surge hoppers below fuel bunkers

- Provision for under bed firing of the Bio-Gas

- Water cooled bed ash coolers

- Electro Static Precipitator (ESP) , EMIGI Rapper type

- ESP inlet/outlet expansion bellows

- Ash door assemblies.

- Air and flue gas fans and draught system

- Two (2) Forced Draught (FD) fans (2 x 60%)

- Two (2) Induced Draught (ID) fans (2 x 60%)

- Two primary air fans (2 x 125%)

- On line O2 analyser

- Higher size fuel transport line, castings & PA Fan with Motor

- 2 nos water cooled bed ash cooler as against 6 nos air cooled bed ash cooler

- Motorized Valve as against manual valve at each feed pump discharge

- All Blowdown second valve should be lever operated

- Pneumatically operated bypass valve for FCV as against Motorized bypass valve for Boiler feed water control station

- 2 nos Bi-colour Multi-port direct water level gauges & 1 No hydrastep (Electronic drum level indicator) to indicate the remote water level indication at operating Floor & Control room.- Yarway control

- Hydraulic type HP dosing pump and LP dosing pump

- Silencer for FD Fan suction

- SA213 T22 material for radiant superheater All coal feeders shall be designed such that boiler performance (100 % MCR) should not affect during one feeder down condition.

- ESP to meet the outlet dust emission level of 50 mg/ Nm3 considering worst coal as basis (i.e. Coal of 5800 Kcal/Kg GCV) with all  field in Service.

- Boiler MCC (Considering 2 x 60 %ID, FD fans, 2 x 125 % PA Fan, 2x 120 % feed Pump, Coal Feeders, LP/ HP Dosing etc). The MCC shall be as per the specifications as  enclosed

- ESP MCC

- Draught gauges for Air Box compartments with panel

- Headless type RTD with 10 mtr Teflon Insulated Cables instead of Head mounted RTD

- Flow switches in sealing water line of Feed  pumps

- Proximity switches for Control Valves, RPC & SOPC

- Additional 1 no Furnace Pressure Transmitter

- Level transmitter instead of level switch in Deaerator

- Additional 1 no Drum Pressure Transmitter

- High level switches for ESP, Air Heater & Economisers ash hoppers

- SS316 of material for all impulse piping

- Flame proof cable glands instead of Industrial area Cable Glands.

- ESP hopper Heaters

- Complete Structure,  GI Grating, Platform, railing, tie beams, supports, Ash Hoppers for the ESP. the ESP Hopper capacity should be for 8 hrs storage.

- Air & Flue Gas Ducting

- All Dampers & expansion bellows

- PA/SA fan suction

- From PA/SA fan discharge up to air heater inlet

- From Air heater outlet up to wind box

- From furnace outlet up to economiser inlet

- From economiser outlet to air heater

- All Control dampers & control valves to be provided with smart valve positioners, position feed back transmitter & pnp type proximity switches to close limit with desired state   under fail safe condition.

- Root valves for all HP Valves

- Air Heater arrangement (Air through tubes)

- Gauge glasses 2 nos near drum, one no hydrastep in control room ( Yarway control)  / Operating floor and 1 electronic level indication in Control room

- Access Door assemblies

- HP dosing system consisting of dosing tanks, associated pumps, motors, piping & valves

- LP dosing system consisting of dosing tanks, associated pumps, motors, piping & valves

- De-aerator cum feed water storage tank

- Sample coolers, blow down tanks & flash vessels

- Feed pumps (electrical) 2 x 120 % MCR capacity along with all valves , including imported ARC valves.

- Feed pump manual suction and motorized discharge isolation valves

- Boiler platform and structure extension of 3000 mm on one side of the boiler and side cladding up to operating floor

- Boiler house, fuel bunkers, all structural, operating platforms, roofs and side cladding with metapoly

- Feed water control stations
-	1 x 100% pneumatic valve
-	1 x 30% pneumatic valve
-	1 x 100% pneumatic bypass valve with leakage class VI

- All auxiliaries like common frames, coupling set and foundation bolts for pumps, motors

- Boiler structural and foundation bolts

- Boiler house front row columns shall be supplied to take the load of both coal conveyors. However, other row of columns and other structures for conveyor supports shall be under Purchaser’s scope. Since coal conveyors shall be located on the front side of the boilers and the first row columns   shall take the load of all the conveyors, first row of columns of second boiler shall also be erected along with the first boiler to erect coal conveyors.

- All the horizontal beams below the chequered plate of the fuel bunkers to take care of the loading of all the fuel conveyors (which are under Purchaser’s scope.)

- Refractory and insulation

- Continuous blow down (CBD) tank

- Intermittent blow down (IBD) tank

- Steam, water, instrument air, cooling water and auxiliary pipe work with valves and fittings up to terminal points

- Boiler filling line with all accessories

- All structure supports from ground floor and tie beams required

- Silencers for S/H steam, start-up vent valves (2 Nos.)

- Monorails for fans, feed pumps

- Monorails for ESP Top for rectifier maintenance

- All drains to the ground floor and to drains to be channel up to battery limit

- All field instruments including control and actuators

- ESP MCC 3 ph, 4 wire, 50 kA, 415 V rectifier transformer and TR set control panels

- ESP system equipment

- LPB station drives

- Overground earthing for ESP equipments up to ground level

- Digital energy meter for ESP MCC and hook up to DCS

- Microprocessor based ESP controller

- PLC based ESP rapping Mechanism

- Motorised valves and actuators

- All LT/HT & integral motors

- All flow meters

- All control dampers with smart electro pneumatic valve positioners

- Bottom mounted bed temperature thermocouples

- Primary elements for feed water flow, steam flow and air flow

- Spares for start-up and commissioning

- All staircases as per industrial standards and no monkey ladders shall be allowed.

- Surge hoppers for all the bunkers

- Motor control centers

- Earthing upto ground level

- Primer painting

- Stress analysis of steam piping upto anchor point, however, supply shall be upto main steam stop valve/NRV

- Target plates required for steam blowing.

- SWAS Package

- All Electrical / instrument GI cable Trays

# 3.1	Scope and Extent of Services

Vendor shall be fully responsible for erection of the items supplied by them and assistance during start-up and commissioning of Equipment. The details of the scope of work and services of the Vendor shall be as given below:

### 3.1.1	Submission of Activity Chart

Vendor shall submit activity chart prior to commencement of erection to depict the activity schedule planned to complete erection, to match with commissioning schedule of Equipment.

## 3.1.2	Receipt and Inspection

Vendor shall be responsible for receipt and unloading of all the erection materials under supply from VENDOR and also arrange to store the materials in the Purchaser's storage yard/temporary storage space of the Vendor.

Vendor shall be responsible for inspection and checking of all the erection materials with the shipping list, consignment note and drawings of Vendor, upon receipt at site and report to Purchaser regarding their correctness and about missing/damaged items.

### 3.1.3	Liaison with Inspectorate of Steam Boilers

Vendor shall be required to carry out liaison work with Inspector of Steam Boilers,

Submission of the relevant documents/certificates such as commencement certificate, progress report, completion report etc., pertaining to erection of pressure parts to Inspectorate of Steam Boilers in compliance with Indian Boiler Regulations (IBR).

Obtaining approval from Inspectorate of Steam Boilers for Vendor and his sub-Vendor for undertaking erection.

Arranging for site inspection of all pressure parts by Chief Inspector of Boilers, prior to commencement of the work and to obtain clearance to carry out work.

### 3.1.4	Deployment of Manpower

Scope of services of the Vendor shall include provision of a team of erection engineers, supervisors, skilled/un-skilled manpower required for erection and commissioning.

### 3.1.5	Boarding and Lodging for Erection Personnel

Vendor shall be responsible for arranging boarding, lodging and conveyance for his entire manpower.

### 3.1.6	Site Construction Facilities

Vendor shall make its own arrangement for construction of site office/temporary store room in the place provided by Jubilant.

## 3.2	Erection (For VENDOR Supplied equipments only)

The erection services of Vendor shall include, but not limited to, the activities highlighted below:

- Vendor shall take delivery of materials from purchaser storage area/Vendor's storage area in sequential order to match with erection sequence.

- All the materials shall be cleaned/wire brushed, prior to erection.

- Minor transit damages on the materials shall be repaired by the Vendor, free of cost.  For major damages, the Vendor shall carry out the repairs at supplier cost.

- However, the repairs, which have been caused due to mis-handling or negligence on the part of Vendor, shall be carried out by Vendor, free of cost.

- Proper records shall be maintained for various critical dimensions/clearances etc., and the copies of such records shall be mutually signed by the Purchaser and Vendor to ensure adherence to the Vendor's recommendations.

- Erection work shall be carried out in the manner and sequence as may be directed by Purchaser's representative/Vendor's recommendation.

- Vendor shall notify Purchaser sufficiently in advance, ensuring the requirement of materials and any other items that are to be supplied by Purchaser.

- Leading of all materials from the Purchaser's storage yard/ Vendor's storage yard to the respective foundations of the material.

- Inspection of the civil foundations of boiler and other equipment, prior to commencement of erection to check dimensions, correctness of grouting the elevations etc.  Deviations, if any, shall be brought to the notice of the Purchaser.

- Pre-assembly of various structural materials, ducting, rotating machinery, as envisaged by Vendor.

- Placement on foundation and in position and subsequent alignment,  checking and cleaning as required, as per detailed specifications, drawings, instructions.  Vendor shall provide stainless/brass shims for final alignment and adjustment, in addition to packing plates.  Number of packing plates shall be kept minimum.  Gas cutting, machining/ grinding of the packing plates to suit the required size, as per Purchaser/Vendor shall be carried out by the Vendor.

- Fabrication and erection of temporary fixtures/piping, like scaffolding, structural frames etc., which are not permanent, but are incidental to erection shall be carried out by Vendor.

- All integral pipe works of boiler shall be as per Vendor's certified drawings.  Minor modifications on pre-fabricated pipes shall also be considered as activity incident to erection work..

- All pressure parts shall be cleaned with compressed air and sponge test, if necessary, shall be carried out to confirm that the tubes are free from choking.

- Supervision of erection Erection, alignment and coupling of motors of various equipment, which are under supply by Purchaser, shall also be carried out by Vendor.

- Vendor shall make necessary action for any mistake during erection, errors made in the drawings, fabrication and transportation.

- Vendor shall also carry out improvements/modifications as suggested by Purchaser & mutually agreed during the course of erection for betterment of layout at no extra cost.

- Welding of pressure parts, high pressure piping and all internal high pressure piping and all internal piping  covered under IBR shall be done by certified welders, duly qualified as per the provisions of IBR.  However, these welders shall be tested at site by Purchaser to ascertain their suitability.

- Welding of pressure parts, tube/pipes, of sizes 63.5 mm dia. and below shall be carried out by tungsten inert gas (TIG) welding and size greater than 63.5 mm dia. shall have root welding by TIG and filling by sub-merged metal arc welding (SMAW).

- Radiography of pressure parts and piping shall be carried out as stipulated in IBR (1950) with latest amendments.

- All alloy steel welding joints on pipes shall be heat-treated/stress relieved, as stipulated by IBR and also as recommended by Vendor.

- All structural and duct welding shall be carried out, utilising electrodes conforming to AWS E 6013.

- Scope of work shall also include erection of such instruments that are necessarily to be fixed/attached to the pressure parts/non-pressure parts.  The necessary power cylinders, hydraulic piping etc., shall also be included in the scope of erection.

- Vendor is fully responsible for lining and insulation work of boiler, piping, covered in the scope.  The details of scope of services shall be:

- Application of various types of refractory, including castables, standard and shaped firebricks, refractory mortar, cement plaster etc., and insulation materials, external sheet casings for Equipment covered under this Contract

- Chipping and cutting of firebricks to suit the site conditions

- Application of insulation covering both application of ready made wool mattresses and preparation and application of specified thickness and shaped mattress like single layer or multi-layer out of loose wool with one side or all sides wire mesh.

- Vendor shall be responsible for provision of all consumables, welding electrodes, oxygen/acetylene gas etc.

- Vendor shall be responsible for provision of tools, tackles, handling devices etc., to carry out the erection.  Vendor shall provide all precision equipments like micro level, dial and other gauges, surface plates, straight edges, radiography equipment, stress relieving equipment etc., for the erection.

- Vendor shall submit every fortnight the progress report to Purchaser for his review.  In case Purchaser feels at any stage that the progress of work needs expediting, so as to ensure completion of work within the stipulated time, Purchaser shall have the right to instruct the Vendor to increase Vendor's manpower.

- Vendor shall keep a competent representative, who will be responsible and shall remain Site In-charge to execute all activities connected with erection.  Vendor shall submit the proposed organisation chart for undertaking erection and commissioning.

- Vendor shall place sufficient number of competent erection engineers/supervisors in addition to Site In-charge.

- Site In-charge shall not abstain himself from site without obtaining permission from Purchaser.

- Vendor shall work under the guidance and directions from Purchaser/ Consultants.

- All statutory rules under Labour Laws prevailing in  Maharashtra shall be observed by the Vendor.

- Vendor shall ensure that his team shall adapt all safety measures to avoid occurrence of accidents.

- Vendor shall work in close co-ordination with building Vendor or other agencies, who will also be working in the same area simultaneously to speed up the overall commissioning.

- Vendor is responsible for making the regular payments to their labour / sub Vendor.

- In case of any accident during the course of the erection, testing, commissioning (VENDOR items supplied), all the responsibility shall be with the Vendor only.

## 3.3	Painting

### 3.3.3	Finishing Paint	- Only Primer painting

### 3.3.4		Pre-commissioning Testing

After completion of erection, the pressure part system of the boiler and piping shall be hydraulically tested to the required pressure.  Vendor shall provide the necessary blanking arrangement for such hydraulic tests.

Vendor shall be responsible for offering boiler pressure parts and piping for statutory hydraulic test in the presence of Inspector of Boilers.

The furnace and ducting shall be subjected to leak test and all leaks shall be attended to, prior to application of insulation.

### 3.3.5	Trials and Commissioning

Vendor shall assist Jubilant during pre-commissioning checks, trial runs of the equipment and commissioning.

Vendor shall also provide, at appropriate time, personnel for pre-commissioning checks, trials and commissioning.

Vendor shall provide, well in advance, to Purchaser various checklists, commissioning procedures and other details for perusal of the Purchaser.

### 3.3.6	Purchaser's Responsibility

Purchaser shall arrange the following items/facilities:

- All civil work like Equipment foundations, brickwork, flooring, structure, platforms, ladder, ducting & bunker etc. & erection of the same which ever is in Jubilant scope

- Necessary water, compressed air, and power at one point at/near the erection site

- Necessary office at Site, as available

- Adequate lighting system at erection site to enable erection and commissioning work to progress throughout twenty four hours in a day

All statutory fees towards IBR shall be borne by Jubilant. However, Vendor shall co-ordinate with Boiler Inspectorate for smooth execution of the works.

Purchaser shall give to Vendor, in due time, any information concerning local laws and regulations which is necessary for proper execution of Contract.

Purchaser shall designate in writing a competent representative to be his channel of communication with Vendor's staff.

# 4.0	BASIS FOR DESIGN

## 4.1	General

Boilers and their auxiliaries are designed and manufactured in full accordance with the relevant codes and regulations and shall be capable of safe and continuous operation under all conditions without strain, vibration or other operational difficulties.

Boilers, their components and associated plant are properly designed and constructed and shall be provided with suitable supports to permit free expansion and contraction without causing leakage or distortion of any item of the equipment.

The analysis of the fuels shall be fully taken into account in the design, and the furnace volume, heat release rates and refractory areas are to be selected suitably.  Other features of the design shall be based accordingly and the erosive effects on the pressure parts and other parts of the boiler shall be minimised by the avoidance of excessive gas velocities and undue carry over.

All parts and components, subject to corrosion, erosion or other deterioration shall be made of materials suitable for the application and an adequate allowance shall be provided in the design for this deterioration.

The design of the boilers and their auxiliaries is such that maintenance requirements are facilitated and that easy access is available to parts and components requiring replacement from time to time.

All equipment shall be suitable for operation under hot and humid tropical conditions..

Noise level shall be less than 80 dB.

## 4.2	Site Data

AMBIENT CONDITIONS:

Plant Elevation above Mean Sea Level (MSL)	:

Temperatures :

*	Maximum Air Temperature		 	: 	43 deg C

*      	Ambient Temperature                                    :  	35 deg C

*	Minimum Temperature			: 	19 Deg C

*	Plant Design Temperature			: 	---

(Performance design)

*	Plant Design Wet Bulb Temperature		:	25 Deg C

*	Plant Design Temperature for Electrical	:	---

Equipment

Relative Humidity :

*	Maximum			: 	99.4

*	Minimum			: 	16.4

*	Plant Design Relative		: 	----

Humidity

Wind :

Wind Direction 			:   West to East for 8 moths &

East to west for remaining 4 months

Design Wind Velocity			:  15 Kmph

Seismic Zone			 : III, as per IS 1893 Rev 3: 1975

Climatic Condition                                :	Hot and Dusty

## Compressed Air

Operation pressure	kg/cm2 (g)4.5

## 4.3.4	Electrical

Power supply for motors:
-	Upto and including 160 kW rating	415 V, 50 Hz, 3 phase
-	>160 kW<1000 kW		11 kV, 50 Hz, 3 phase

Below 0.25 kW :
-	Non-critical		240 V, 50Hz, single phase
-	Critical		415V, 50 Hz, 3 phase

Control voltage for motor control		240, 50 Hz, AC
centres and circuit breakers

Trip supply for breakers		110 V DC
Control voltage for instruments		240 V, 50 Hz, AC
Voltage for power sockets and illumination	240 V, 50 Hz, AC
Voltage power supply to converters		415 V, 50 Hz, 3 phase

Voltage for integral motors supplied 		415 V, 50 Hz, 3 phase
along with the equipment

## 4.4	Instrumentation

Type of Instruments	Control valves (Pneumatic/Electrical 	
	motorised) ,rpcs,sopcs,analyser , temp

Sensors, smart field instt, VFD etc

Electronic Field Instruments,
	Smart type (HART Protocol), 2 wire 	system wherever possible

Level of instrumentation	To suit plant operation from  
 	DCS

## 4.5	Piping

All steam piping and valves shall be as per ANSI Standard.

# 5.0	APPLICABLE ACTS AND REGULATIONS

The design, materials and construction of the boilers should be in accordance with Indian Boiler Regulations (IBR) 1950, (with the latest amendments), International Standard Organisation Code (ISO) and Vendor shall be responsible for obtaining the approval for the boiler under IBR.

In this connection, Vendor shall take appropriate steps from the design stage by providing the necessary drawings, certificates, design calculations, material fabrication details and all other information required by Indian Boiler Regulations, duly approved by the Inspectorate of Steam Boiler, Punjab, India.  Copies of all such submissions shall also be sent in triplicate to Purchaser.  The provisions of IBR shall be considered as the minimum requirements and Vendor shall include any additional measures considered necessary for safe operation of the boilers.

Radiograph inspection and heat treatment of pressure parts in the manufacturer's works shall be in accordance with IBR.

Similarly, all relevant provisions of Indian Factories Act, Indian Explosives Act and all other applicable requirements shall be observed in the design and manufacture.

All costs incurred in complying with these acts, rules and regulations shall be borne by the Vendor.

# 6.0	DETAILED SPECIFICATION

## 6.1	Boiler Pressure Parts

### 6.1.1	Steam Drum

Steam drum shall be of all welded construction, completely radiographed to prove weld soundness, stress relieved and hydraulically tested.  The drum shall be fabricated from boiler quality plate to the appropriate specification and constructed in accordance with IBR.

Steam drum shall be provided with suitable dished-ends and manholes,  with a swing type opening internally and internal extension pipes shall be fitted in the drums as appropriate to ensure uniform distribution or collection for the duty involved.

Steam drum shall have manifold connections to the superheater headers.  Nozzles shall be provided for the external mounting of safety valves, water level gauges, water level alarms, water level regulators, pressure gauges, continuous blow down, feed water inlet, chemical injection, sampling, air vent and any other uses of steam from the drum.

The steam drum shall be provided with effective means for ensuring separation of water particles from the steam comprising a girth baffle, and a two stage system of vortex separators and chevron scrubbers or the like to produce steam with a purity better than the following:-

Silica		less than 0.02 ppm
Iron		less than 0.02 ppm
Copper		less than 0.003 ppm

### 6.1.2	Furnace Tubes and Headers

Furnace tubes shall be of seamless carbon steel conforming to ASME Standard or equivalent.  Tubes connecting to the steam drum shall enter radically.  Tube ends terminating at headers shall be welded to stub tubes provided on the headers.

The furnace shall be of fully water cooled construction comprising membrane walls with integral fins and welded gas tight.  Refractory linings, ignition and burn-out arches shall be employed, as required by the design, and shall be fully detailed.

The headers shall be designed and manufactured in accordance with IBR and shall be of adequate size and of seamless carbon steel conforming to ASME Standards or equivalent with welded end caps.  The necessary drain connections, peep-holes and hand-holes shall be provided as required.

Connections to the steam drum and connections to the headers shall be designed so as to form an integral circuit providing adequate natural circulation under all operating conditions.

All fittings and supports, supply and riser connections and the necessary access, inspection and burner ports shall be provided.

### 6.1.3	Superheaters and Desuperheater

The superheaters shall comprise primary and secondary sections located appropriately in the radiant and convection zones and shall be complete with all manifolds, fittings, supports, supply and drain connections and inter-connecting piping.

The superheater tubes shall be seamless with the tube materials conforming to ASME Standard or equivalent, selected to suit the superheater metal temperatures and the method of suspension shall be designed to permit free expansion.

Where the superheater metal temperatures shall be high enough for creep to be a consideration, the tube dimensions and materials of construction shall be selected to give a design creep life in excess of 100,000 hours.

De-superheater, of spray type, shall be provided in the steam flow between the primary and secondary superheaters and shall be controlled from the superheater outlet temperature.  The secondary superheater outlet temperatures shall, preferably, be the highest steam temperatures in the system.

Spray water shall be derived from the feed pump discharge only. The pumps shall be of multi-stage centrifugal type with hydraulic balancing of the stages and shall be complete with gland sealing, lubrication and bearing cooling arrangements.

### 6.1.4	Economiser

The economiser shall be of bare tube construction with seamless carbon steel tubes conforming to ASME Standard or equivalent and of continuous loop type with inlet and outlet headers.  The economiser units shall be supported in a structural steel frame and enclosed within a 5 mm thick welded steel casing.  Doors shall be provided for observation and also to obtain access for maintenance.

The economiser shall be complete with necessary drains, vents, thermometer pockets and pressure gauge connections.

### 6.1.5	Boiler Mountings and Fittings

The boiler shall be provided with a complete set of mountings and fittings, of reputed make, in accordance with Indian Boiler Regulations for the safe operation of the boiler and the following shall be included, without limitation.  Root valves shall be provided for all HP valves.

### For Steam drum

-	Safety valves	
-	Continuous blow down valves 	
-	Direct water level gauge with isolating valves
-	Hydrastep  (Yarway control)
-	Air vent valves
-	Pressure gauge with isolation valves (2 Nos with 10 “ Dial Size)
-	Chemical dosing valve and check valve
-	Valves for auxiliary supplies
-	Sampling valves
-	Valves for all impulse piping
-  	Sample piping

### For Feed Water Line

-	Regulator valve
-	Isolation valves for regulator
-	Regulator by-pass valve
-	Feed water regulator drain valve
-	Non return valve
-	Pressure gauge isolation valves
-	Thermometers with thermowells

### For Headers

-	Air vent valves
-	Drain valves
-	Blow down valves

### For Economiser

-	Isolation valve
-	Air vent valve
-	Thermometer
-	Drain valve
-	Pressure gauge with isolation valve

### For Superheater Header

-	Safety valve of reputed make along with silencer
-	Motor operated main steam stop valve with bypass
-	Main steam non-return valve
-	Motor operated start-up vent valve with isolation valve and silencer
-	Air vent valves
-	Pressure gauge with isolation valves
-	Thermometers
-	Sampling valves

Note: All isolation of high steam and water lines will have two valves in series.

## 6.2	Fuel Firing and Ash Removal System

In view of the different fuels to be fired in the boiler, Vendor is required to apply his knowledge and proven experience to provide necessary fuel firing/ash removal system/ equipment, which he considers suitable in all respects for the present application.

This section of the specifications, therefore, outlines certain principles that may be followed by Vendor but Vendor may adopt or modify them in whole or in part in the proposals he puts forward with specified guarantees.

Vendor shall describe and justify his proposed design and submit the necessary additional schedules to define the main parameters and materials of construction of the equipment included.

### Solid Fuel Firing System

#### Fuel Bunker and Chute

Indigenous coal, Imported Coal.

- Boiler shall be provided with a separate welded mild steel overhead live storage bunker for indigenous coal, imported coal with effective storage capacity for 24hrs operation,.  Water volume of bunker of boiler  will be accordingly.

#### Solid Fuel Firing System

Boilers shall adopt fluidised bed combustion system of proven type with underbed fuel feeding system, selected based on the fines content of fuel specified.  Evaporator coils may be immersed in the fluidised bed as applicable and coils shall be properly studded and spaced out to avoid erosion.  Both fuel and air nozzles shall be of stainless steel.  Vendor shall fully describe the feeding system selected, highlighting the salient features.  Vendor shall consider underbed feeding system for imported coal

Fuel feeding system shall be arranged with suitable variable frequency drives (VFD) for underfeeding systems.

## 6.3	Boiler Ash and Dust Discharge System

The boiler shall be provided with ash drainpipes suitable for discharging the ash.

If required by the design, hopper shall be provided to collect the dust from different outlets, either for re-firing or for disposal, as applicable.  The hoppers shall be constructed of mild steel plate of adequate thickness with suitable reinforcement and support.   Air lock, rotary valves shall be provided at the outlets of chutes and hopper, as applicable.  Necessary ash coolers (water Cooled) shall be provided to cool the ash to around 150°C for further disposal. The ash analysis shall be given for the convenience of ash handling system.

Vendor shall describe the ash/dust removal system proposed and indicate clearly the terminal points considered for supply.

## 6.4	Electrostatic Precipitator

Vendor shall include one (1) electrostatic precipitator for boiler to meet the allowable dust emission as stipulated by the latest Pollution Control Standards (as applicable to the State , India) limiting the dust concentration not exceeding 50 mg/Nm3 (dry) with all field in service & VENDOR will indicate the emission level during any one field out of service. Scope of supply shall also include rectifier, transformers hopper low & high level monitoring and controls etc along with supporting structure, hoppers, heaters, MCC etc.

Vendor shall fully describe the sizing philosophy adopted and shall furnish the details on emitting and collecting system with material of construction.

The elevation of hopper outlet flange shall be at +3.5 m from finished floor level.

The jubilant scope of work for ESP shall be Civil work based on Load data,

## 6.5	Air and Flue Gas Systems

### 6.5.1	Combustion Air Distribution System

Combustion air distribution system shall be specifically designed for the proposed fluidised bed firing.  The design of the proposed distribution and the means for controlling the air admission shall be fully described.

### 6.5.2	Fans and Draught System

Boiler shall adopt balanced-draught system with 2x60% induced draught (ID) fans and 2x60% forced draught (FD) fans and 2x125% primary air fans/secondary air fans. Both ID and FD fans shall be provided with damper. Vendor should state, in the Schedules, the design basis for the fans and the margins incorporated in the fans for the design head and capacity.  The fans shall be designed with the latest technology to achieve maximum efficiency and shall be provided with necessary control dampers with actuators.  fan and motor may be mounted on a common base frame and provided with flexible coupling and guard.  Motor shall be procured and supplied by VENDOR.  However, coupling halves for motor and fan with bolts and nuts and foundation bolts shall be included in Vendor's scope of supply.  Coupling halves shall be properly balanced.

Suction for the FD fan shall be taken at sufficiently high level to avoid entrainment of floor surface dust and Vendor shall select suitable location.  Locating venturi type metering in the suction duct is preferred for air flow measurement.

The ID fan shall be designed and constructed to resist erosion. Vendor should state the features incorporated in this respect.  Isolating damper shall be provided at the fan discharge to the chimney.

All fans except ID fan shall be designed to run at 1440 /1500 rpm or less and the ID fan shall be designed to run at 1000 rpm.  Vendor shall provide characteristic curves for the pump, fans and other equipment.

Purchaser may also decide to install variable frequency drives for all the fans/pumps at later date wherever appropriate.  Hence, fans/pumps etc. shall be selected suitably.

### Air Heater

If required by the design, boiler shall be provided with a tubular air heater along with economiser to recover heat from flue gas and pre-heat the combustion air, limiting the flue gas temperature not exceeding 150°C, when leaving air heater. The air heater shall comprise ERW annealed tubes conforming to BS-1775 or equivalent, suitable for expansion and complete with tube plates, supports, casing, dampers .

Vendor shall clearly state the proposed operation of the air heater on the different fuels and the appropriate flue gas outlet temperatures shall be stated.

### Duct Work and Dampers

- Boiler shall be complete with necessary cold air, hot air and flue gas ducting required for all purposes.The ducting shall be constructed of mild steel sheet, as necessary, with angle iron end frames, and the joints made gas/air-tight by means of suitable gaskets.  The air and flue gas ductings shall be adequately stiffened and supported to withstand the pressures involved and to prevent vibration.  Necessary intake silencers, grills, access doors, expansion bellows and isolating devices shall be provided.  External cleats shall be fitted to hot ducting to facilitate the application of lagging.  All ducting should be above the finished floor level.

Flue gas velocity in the ducts shall not exceed 12 m/s.

Necessary heavy duty dampers and bypass dampers shall be provided complete with actuators, visual position indicators and means of securing as required by the design.

### Chimney (RCC)

The Purchaser shall construct the RCC Chimney. However the Vendor shall provide the Diameter, Height and GA Drawings of the same

## Feed Water System

Feed water system of the boiler shall comprise 2 x 120% MCR feed pumps, HP chemical dosing system and connected control stations and piping.  The details of the system are further described below.

### 6.6.1	Deaerator and Feed tank

#### Deaerator

A deaerator-cum-feed water tank shall be included in the scope of supply with DM water temperature around 27°C, outlet as per design and to limit O2 content in the feed water outlet not exceeding 0.007 ppm.  Deaerator shall be supplied with heat recovery system, level control system, overflow system, temperature control system, safety valves and other fittings.  Deaerator shall have the stubs necessary for the following.

##### 6.22	DEAERATOR, FEED STORAGE TANK; PIPING, VALVES AND FITTINGS

##### The Deaerator, Feed Storage Tank, the Feed pumps with the drive system shall be supplied by Vendor , and will be briefly as below:

##### 1.	DEAERATOR

##### -	Type								-	Spray cum Tray

##### -	Arrangement						-	Cylindrical, Vertical Flange

##### Mounted over Feed Storage Tank-

##### Size                                                          -Vendor to be specify

##### -Max. Capacity (110% Boiler MCR)-		 TPH

##### -Operating pressure and temp.		-	0.232 Kg/cm2g (105°C)

##### -Design pressure					-	2.5 Kg/cm2g

##### -	Design Code			-	ASME Sec VIII Div.1

##### Boiler 100% MCR	110% MCR

##### -	At minimum temperature of 27°C,

##### (100% DM Water)

##### DM water 		Flow 	TPH

##### -	Auxiliary steam 	Flow	TPH				-	Total Deaerated water

##### flow to boiler (including

##### BD): at 105°C				TPH

##### The Deaerator will be complete with all the connected piping (Auxiliary steam & DM Water) Valves and Fittings, all as shown in the P&ID. The DM Water & auxillary Steam piping shall be done by Jubilant upto Control valve inlet. 2 spare water inlet nozzle to be provided at de-aerator for 100 % flow.

##### -	The Spray nozzles and Trays of deaerator will be of Stainless steel.

##### The Deaerator has been designed and sized considered the following worst case (as desired).

##### DM water at 27°C (min. temperature level), at 2.5-3 kg/cm2g (min. pressure) at the inlet of Level Control valve unit, near the Deaerator unit.

##### b) Auxiliary steam at 4.0-5.0 Kg/cm2g to be supplied from control valve inlet, for deaeration and Feed heating at the Deaerator Pressure Control valve unit inlet (max. 13 TPH at 110% MCR).

##### 2.	FEED STORAGE TANK

##### -Type / Arrangement; Location	-	Horizontal, Cylindrical

##### -Supports arrangement 			-	2 No. Saddle supports;

##### FW Tank unit placed on the roof of the independent support based on the NPSH requirement.

##### -Size approx.: ODxShell			-	vendor to be specify

##### - Capacity of water holding (as	 -	20 Min.Storage at 110% MCR

##### Specified) (between NWL and Trip)

##### -	Operating pressure and temp.		-	0.5 Kg/cm2g; 105°C

##### Design pressure					-	2.5 Kg/cm2g

##### -Design code					-	ASME Sec VIII Div.1

##### The Feed Water Storage Tank will be complete, with all the connected piping, valves and fittings

##### The Feed tank has been sized for 110% Boiler MCR conditions, and with 20 min. water holding capacity – between NWL and Trip level – with 60% tank height.

##### 3.	ARRANGEMENT / LOCATION OF FW STORAGE TANK AND FEED PUMPS

- 1) The Feed water storage tank (with the Deaerator mounted and supported on this tank) – will be placed over independent structure, at required NPSH level.

##### 2) The 2 x 120% Feed pump will be located at Ground level

### Feed Pumps

2 x 120% MCR electrically driven feed pumps (one running and one stand-by for boiler) shall be supplied for the power boiler.  Pumps shall be of multistage centrifugal type, complete with balance chamber and necessary suction and delivery valves, non-return valves and leak-off valves to cater to start-up and low flow conditions, gland sealing and bearing cooling pipe work, valves and flow indicators.  The feed pumps leak-off lines shall discharge to the deaerator via isolating and non-return valves.  The pumps shall be supplied with necessary suction and discharge lines. Auto Recirculation Valve (ARC) of imported make shall be provided.  All the piping like leak valves, minimum discharge lines along with isolation, NRV etc. from feed pump up to deaerator shall be included in the scope of supply of Vendor.

The pump and motor shall be mounted on a common base frame and provided with a flexible guard. However, coupling halves bolts/nuts and foundations bolts for motor and pump shall be included in Vendor's scope of supply. Coupling halves shall be properly balanced. One (1) tapping with an isolation valve shall be provided on the discharge header of boiler feed water pumps to supply feed water to 105 ata for Desuperheating Station. The size of the tapping shall be suitable for a flow of 15 tph at boiler feed pump discharge pressure.

### Feed Water Control System

The control station shall be provided for drum level control with smart electro-pneumatic control valve, isolating valve, bypass valve, drain valve etc.

### Chemical Dosing

Vendor shall include suitable HP and LP chemical dosing systems and the same shall be supplied with mixing tank, pumps, piping, valves and fittings.  HP and LP chemical dosing tanks and piping shall be of stainless steel. HP dosing system shall have two (2) pumps for boiler (one running and one stand-by) and LP dosing system shall have two (2) pumps (one (1) running and one (1) stand-by) common for the boiler. DM water piping from one point in the Boiler area.

### 6.6.6	Sampling Lines and Coolers

Sampling lines shall be provided for feed water, drum water, saturated steam and superheated steam.  Sampling lines and nozzles shall be of stainless steel.

## 6.7	Boiler Structure and Other Accessories

### 6.7.1	Boiler Structure

Boiler shall be provided with necessary supporting structures from ground level. The structures shall be fabricated from rolled steel sections to support the boiler, air distribution system and other auxiliaries.  The structures shall incorporate necessary columns, beams, overhead steelworks and supports,

Boiler shall be provided with necessary platforms, ladders, stairways and support steelworks to facilitate safe access to all parts of the boiler for operational and maintenance purposes.

The structure shall incorporate necessary lifting beams and hoist blocks wherever required for maintenance purposes.  All the design and details shall be as per relevant IS Code.

### 6.7.2	Refractory and Insulation

Refractory and insulation of the boiler and its auxiliaries shall be complete with necessary castable refractory, refractory bricks and blocks as required by the design, together with requisite fixings, holders and other attachments.  The refractory and insulation materials shall comply with relevant Indian Standards.

Boiler furnace area shall be neatly covered with mineral wool mattress of acceptable quality and required thickness and cladded with corrugated aluminium sheeting of thickness not less than 22 SWG (VENDOR shall consider corrugated aluminium cladding sheet of 22 SWG thk for water wall and plain aluminium cladding sheet of 22 SWG thk for other zone).  The maximum skin temperature of the casing shall not exceed 10°C above ambient when the boiler is operating at MCR.  The exposed portions of the boiler drums, integral pipe work, casing of economiser, air heater, steam and feed water lines shall be provided with necessary insulation and clad with aluminium sheeting neatly attached, so as to limit the skin temperature to 10°C above ambient.   Removable insulated boxes shall be provided for valves and provision shall also be made for easy removal of the insulation at flanges without affecting the general pipe work insulation.

All drain lines, vent and exhaust lines and all other components at high temperature shall be covered with a sufficient thickness of insulation for personal safety.

Necessary seals, expansion joints, door linings, fire clay and fire cement and all other items to complete the installation shall also be included.

Vendor should describe the proposed arrangement of refractory and insulation of various sections.

### 6.7.3	Soot Blowers

Soot blowers, if required shall be supplied by the Vendor.

### 6.7.4	Blow Down Tanks

One (1) IBD tank and one (1) CBD tank for the boiler. Separate IBD & CBD blow down tanks of adequate capacity & both the tanks should be connected with level control shall be provided to receive all intermittent and continuous blow down and all other drain discharges from the boilers.  Tanks shall be supplied with supports and vent of adequate size.  Vent pipe shall be extended at least 10 m from the top of the tank.  Vendor shall also make provision for utilising flash steam of blow down tank in deaerator or elsewhere.

### Foundation Bolts

All foundation bolts, fixings and attachments shall be included in Vendor's scope of supply for the items supplied by VENDOR.

### 6.7.6	Consumable Materials

Vendor shall provide a specification for all consumable materials required for satisfactory operation of the plant.

### 6.7.7	Special Tools

A pneumatic operated expander with sufficient set of mandrill shall be provided to cover the full range of tubes together with a set of other special tools and tackles required for the erection and maintenance of the boiler.

### 6.7.8	Start-up and Commissioning Spares

Vendor shall provide free of cost to Purchaser all Spare Parts that may require replacement at the time of Start-up and Commissioning of Equipment.

## 6.8	Piping, Valves and Fittings

All the integral pipe work associated with the boiler shall be provided including the necessary valves including motorised main stop valve, along with motor and integrated bypass valve motorised start-up vent valve, fittings, flanges, gaskets, nuts, bolts, clips, hangers and all other items required to complete the installation.

Adequate means for accommodating expansion shall be incorporated as appropriate. All HP valves shall be provided with a root valves.

The pipe work shall include:

- Suction pipe work of feed pump from outlet flange of deaerator- cum- storage tank outlet to suction of pumps.

- Discharge pipe work of feed pumps discharge nozzles to feed water control system

- Piping connecting feed water control station and economiser.

- Piping between economiser outlet and steam drum.

- Desuperheater and economiser recirculation pipe work, as required by the design.

- Superheated steam piping including main steam stop valve & non-return valve.

- Superheater safety valve discharge pipe work to atmosphere, including exhaust silencer.

- Drum safety valve discharge pipe work to atmosphere, including exhaust silencer.

- Start-up air vent, discharge pipe to atmosphere including silencer.

- All air vent piping.

- Feed water and boiler drum water sampling pipe work.

- Superheated steam and saturated steam sampling pipe work.

- HP chemical dosing pipe work.

- LP chemical dosing pipe work.

- All blow down pipe work.

- All drains from steam lines, headers and all other drain lines and collecting manifolds to blow down collecting tank.

- All cooling water and service water pipe work from common supply point and to drain.

- All instrument air pipe work from common supply point.

- HT/LT Electric Motors

Vendor shall provide all integral electric motors, like motorised valves,  etc. forming part of the equipment.  Vendor shall also include necessary couplings, base frame, foundation bolts for the equipment and motors

## 6.9	Instrumentation and Controls

### General

Boiler shall be provided with proven control system together with necessary instruments as required by appropriate regulations and also for fail safe and efficient operation. Equipment incorporated shall be of electronic type excepting control valves and damper actuators, which shall be of pneumatic type.

Purchaser has plans to operate the boilers with DCS incorporating all the controls and execution of safety and sequence logics as recommended by the boiler Vendor. DCS shall be provided by Jubilant.

### 6.9.2	Type of Instrumentation

All the instruments shall be of proven design and shall be of a high degree of reliability.

Instruments shall be of state-of-art-technology and be of the latest design.

They shall be of SMART version with Hart protocol.

Revamped/retrofitted components are not acceptable.

The instruments selected shall be the best suited to the process application for which they are used.

Control valves shall be properly sized to handle the flow and the metallurgy shall be suitable for the process conditions in which they are installed.  They shall have pneumatic valve positioners.

All control valves shall have position indicators for feed back in system.

All on-off valves shall have end position proximity switches to monitor the open/close position.

Vendor’s responsibility includes terminating all the field devices in their respective Junction Boxes.

Adequate sampling points, as necessary, shall be indicated for any analytical instruments used.

All field instruments, control and on-off valves, analytical instruments shall be in the scope of Vendor.

All controls shall be from DCS.

All thermowell design temperature shall be 1.5 times more than operating temperature.

It is Vendor’s responsibility to provide control and safety logics for implementation in DCS. This shall be verified and certified by Vendor during Factory Acceptance Test at DCS Vendor’s works.

For any speciality instrument, specific to Vendor’s Equipment, which is not part of Vendor’s list, Purchaser’s prior approval is to be obtained before ordering.

Vendor shall include consumables and commissioning spares as part of the supply.

Erection of VENDOR supplied equipments, erection supervision, start-up and training shall be in VENDOR scope

All field instruments shall be in Vendor’s scope.  Vendor shall attach a list of instruments under his scope including make, type, etc.

Field analog signals shall be 4-20 mA isolated.

Analog outputs from system shall be 4-20 mA.

Field digital input shall be integrated by 24 V DC from system. MCC digital input to system shall be 220 V AC.

All field transmitters will be of 2 wire type; wherever necessary, 4 wire transmitters shall be powered by  220 V AC from UPS.

Vendor shall give approximate I/O count for the instrumentation.  Actual count can be decided during detailed engineering.

All instruments shall be offered from the approved Vendor list by Purchaser. Deviation, if any, shall be only with prior approval of Purchaser.

Local gauges are to be provided as necessary.

Inputs to DCS shall be so selected by Vendor to offer suitability of trending and computation of alarm in DCS.

Furnace pressure measurement shall have redundancy pressure transmitter.

ESP control system shall have RS 485 connectivity to interface with main DCS for monitoring purpose.

The philosophy of operation and control of power boilers shall be based on co-ordination of all plant items from a Central Control Room.

Electronic transmitters of smart type shall be provided including temperature measurement.  All RTD and thermocouple temperature elements shall be provided with a 2 wire, 4 - 20 mA DC transmitter.

Flow instrumentation shall incorporate temperature and pressure compensation as applicable.

All I/P converters shall be of field mounted type.

Two (2) wire signal transmission with a signalling range of 4 to 20 mA DC is to be adopted between field and control room instrumentation.  Control and monitoring shall be capable of accepting transmitter outputs without requiring external signal conditioning.

### Details of Controls for boiler operation

These shall comprise the following but not limited to:

- Three element drum level control system with two out of three logic signal processing along with high and low alarms for drum level.

b)	Two element temperature control for steam temperature control with attemperator control valve and final superheater system.

- Furnace pressure control regulation of ID fan damper.

- Combustion control system to control fuel feed flow by means of fuel feeders speed control, so as to maintain a constant pressure at the outlet of NRV of main steam line.  Flue gas excess oxygen trimming shall be included in the combustion control loop.

Proposed control systems and the schemes of instrumentation with all logic controls for safe operation of the boilers and their auxiliaries shall be fully described by Vendor.

#### Type of Instruments / primary sensors

Primary sensors for steam flow shall be flow nozzle and for feedwater flow shall be orifice plate with carrier rings.

All control valves shall be provided with valve positioners and shall be designed for supply air pressure of 4.50 kg/cm2 (g).

All control valves shall be provided with reputed make I/P converters for converting 4-20 mA control signal to necessary pneumatic signal range as per boiler Vendor’s control logic scheme.

All ON/OFF valves / control valves, required for the boiler protection logic scheme shall be provided with limit switches for closed position.

For pneumatic ON/OFF valves, solenoid valves shall be provided by Vendor and the coil shall be rated for 24 V DC.

All motorised ON/OFF dampers/valves shall be provided with all safety switches for stopping the motor at the end positions as well as torque switches for protecting the motor in case of jamming of the damper/valves.

Impulse piping and all the tapping points with protective wells required for fixing the instruments shall be included in Vendor's scope of supply.

### Parameters to be Monitored in General

The instrumentation supplied shall generally cover the monitoring of the following parameters, but not limited to:

a)	Superheated steam	1)	Temperature
		2)	Pressure
		3)	Flow
b)	Steam drum	1)	Level
		2)	Pressure

c)	Attemperator	1)	Steam temperature before 
 			de-superheater
		2)	Steam temperature after 
 			de-superheater

d)	Drum level local indication	1)	Yarway or equivalent drum 
 			level indicator shall be 				provided near the fireman                                                                                        floor/Control room.
 		2)	This instrument shall include 
 			potential free contacts for 
 			low/high alarms and very
			low/very high drum level 
 			tripping logic.

e)	Feed water	1)	Feed pump suction pressure
		2)	Feed pump discharge pressure
		
		3) 	Feed water pressure at 
 			economiser inlet 				4)	Feed water flow
		5)	Feed water temperature before 
 			economiser
		6)	Feed water temperature after 
 			economiser

f)	Fuel	Coal/ feeder speed

g)	Furnace	1)	Bed height
		2)	Bed temperature
		3)	Furnace pressure
		4) 	Furnace temperature

h)	Combustion air	1)	Pressure at FD/PA outlet
		2)	Pressure at air heater inlet
		3)	Pressure at air heater outlet
		4)	Temperature at air heater inlet
		5)	Temperature at air heater 
 			outlet
		6)	Flow

i)	Flue gas	1)	S/H inlet temperature
		2)	S/H outlet temperature
		
		3)	Temperature after economiser
		4)	Pressure after economiser
		5)	Temperature after air heater
		6)	Pressure after air heater
		7)	Temperature after ESP 
		8)	Pressure after ESP
		9)	Oxygen % (O2 Analyser)
		10)	Pressure after ID fan

# 7.0	TECHNICAL SCHEDULE

| Sl No | Description | Unit | * Vendor to be Provide |  |
| --- | --- | --- | --- | --- |
| 7.1 | Summary of Heating Surface |  |  |  |
|  | Combustion chamber | m² | * |  |
|  | Bed evaporator | m² | * |  |
|  | Superheater | m² | * |  |
|  | Bed superheater | m² | * |  |
|  | Boiler bank | m² | * |  |
|  | Economiser | m² | * |  |
|  | Sub-total | m² | * |  |
|  | Air heater | m² | * |  |
|  | Total | m² | * |  |
| 7.2 | Combustion Chamber Details |  | * |  |
|  | Water wall construction: |  | * |  |
|  | - Width | m | * |  |
|  | - Depth | m | * |  |
|  | - Mean height | m | * |  |
|  | Volume | m³ | * |  |
|  | Furnace volumetric heat release rate | kcal/m3/h | * |  |
| 7.3 | Gas Velocity Data |  |  |  |
|  | Bed | m/s | * |  |
|  | Superheater | m/s | * |  |
|  | Bank tube | m/s | * |  |
|  | Economiser | m/s | * |  |
|  | Air heater | m/s | * |  |
|  | Ducts | m/s | * |  |
|  | After ESP | m/s | * |  |
| 7.4 | Steam Drum |  |  |  |
|  | Design code |  | * |  |
|  | Construction |  | * |  |
|  | Material Specification |  | * |  |
|  | Inside diameter | mm | * |  |
|  | Thickness | mm | * |  |
|  | Overall length | mm | * |  |
|  | Details of steam drying equipment |  | * |  |
| 7.5 | # Tubes, headers and Downcomers |  |  |  |
|  | Design code |  | * |  |
| 7.5.1 | Bed Coils |  | * |  |
|  | Material specification |  | * |  |
|  | Tube OD | mm | * |  |
|  | Tube thickness | mm | * |  |
|  | Tube spacing | mm | * |  |
|  | Special provisions, if any |  | * |  |
| 7.5.2 | Furnace Tubes |  | * |  |
|  | Material specification |  | * |  |
|  | Tube OD | mm | * |  |
|  | Thickness | mm | * |  |
|  | Tube spacing | mm | * |  |
|  | Heating surface | m² | * |  |
| 7.5.3 | Water Wall Headers |  | * |  |
|  | Location |  | * |  |
|  | Outside diameter | mm | * |  |
|  | Thickness | mm | * |  |
|  | Material specification |  | * |  |
| 7.5.4 | Downcomer |  | * |  |
|  | Quantity | No. | * |  |
|  | Outside diameter | mm | * |  |
|  | Thickness | mm | * |  |
|  | Material specification |  | * |  |
| 7.5.5 | Circulation Ratio |  | * |  |
| 7.6 | Superheater |  | * |  |
| 7.6.1 | Primary Superheater |  | * |  |
|  | Design code |  | * |  |
|  | Type |  | * |  |
|  | Material specification : |  | * |  |
|  | - Tubes |  | * |  |
|  | - Headers |  | * |  |
|  | Tube OD | mm | * |  |
|  | Tube thickness | mm | * |  |
|  | Heating surface | m² | * |  |
| 7.6.2 | Secondary Superheater |  | * |  |
|  | Design code |  | * |  |
|  | Type |  | * |  |
|  | Material specification : |  | * |  |
|  | - Tubes |  | * |  |
|  | - Headers |  | * |  |
|  | - Inlet |  | * |  |
|  | - Outlet |  | * |  |
|  | Tube OD | mm | * |  |
|  | Tube thickness | mm | * |  |
|  | Heating Surface | m² | * |  |
| 7.6.3 | Bed Super Heater |  | * |  |
|  | Type |  | * |  |
|  | Material specification : |  | * |  |
|  | - Tubes |  | * |  |
|  | - Headers |  | * |  |
|  | - Inlet |  | * |  |
|  | - Outlet |  | * |  |
|  | Tube OD | mm | * |  |
|  | Tube thickness | mm | * |  |
|  | Header Dia | mm | * |  |
|  | Heating Surface | m² | * |  |
| 7.7 | Desuperheater |  | * |  |
|  | Type |  | * |  |
|  | Location |  | * |  |
| 7.8 | Economiser |  | * |  |
|  | Design code |  | * |  |
|  | Type |  | * |  |
|  | Material specification |  | * |  |
|  | - Tubes |  | * |  |
|  | - Headers |  | * |  |
|  | No. of tubes/assembly | No. | * |  |
|  | No. of assemblies | No. | * |  |
|  | Tube OD | mm | * |  |
|  | Tube thickness | mm | * |  |
|  | Heating surface | m2 | * |  |
| 7.9 | Air Heater |  | * |  |
|  | Design code |  | * |  |
|  | Type |  | * |  |
|  | Material specification |  | * |  |
|  | Tube configuration |  | * |  |
|  | No. of tubes | No. | * |  |
|  | Tube OD | mm | * |  |
|  | Tube thickness | mm | * |  |
|  | Heating surface | m² | * |  |
|  | Means proposed to prevent acid corrosion |  | * |  |
| 7.9.1 | Temperature at MCR |  | * |  |
| 7.9.1.1 | Water |  | * |  |
|  | Water leaving deaerator | °C | * |  |
|  | Water entering economiser | °C | * |  |
|  | Water leaving economiser | °C | * |  |
| 7.9.1.2 | Steam |  | * |  |
|  | Steam temperature at steam drum | °C | * |  |
|  | Steam temperature at SH primary inlet | °C | * |  |
|  | Steam temperature at SH primary outlet | °C | * |  |
|  | Steam temperature at SH secondary inlet | °C | * |  |
|  | Steam temperature at SH secondary outlet | °C | * |  |
|  | Steam temperature at IBSH inlet | °C | * |  |
|  | Steam temperature at IBSH outlet | °C | * |  |
| 7.9.1.3 | Air |  | * |  |
|  | Air entering air heater | °C | * |  |
|  | Air leaving air heater | °C | * |  |
| 7.9.1.4 | Flue Gas |  | * |  |
|  | Furnace outlet | °C | * |  |
|  | Superheater inlet | °C | * |  |
|  | Superheater outlet | °C | * |  |
|  | Economiser inlet | °C | * |  |
|  | Economiser outlet | °C | * |  |
|  | Airpreheater inlet | °C | * |  |
|  | Airpreheater outlet | °C | * |  |
| 7.10 | Ash Cooler |  | * |  |
|  | Type |  | * |  |
|  | No. of coolers |  | * |  |
|  | Material of construction |  | * |  |
| 7.11 | Fuel Firing Equipment |  | * |  |
| 7.11.1 | Fuel Feeder (Coal) |  | * |  |
| 7.11.1.1 | Under feed for Coal |  | * |  |
|  | Type of feeder |  | * |  |
|  | No of feeders: |  | * |  |
|  | - Drag chain | No. | * |  |
|  | - Drag chain | tph | * |  |
|  | Drive details | kW | * |  |
|  | Drive details | kW | * |  |
| 7.11.1.6 | Fuel Oil Firing System |  | * |  |
|  | Burners |  | * |  |
|  | - No. of burners | No. | * |  |
|  | - Capacity per burner | kg/h | * |  |
|  | - Type |  | * |  |
|  | - No. of lances |  | * |  |
|  | - Start-up oil consumption | litres | * |  |
|  | - Location |  | * |  |
|  | - Fuel oil tank | m³ | * |  |
| 7.11.2 | Fuel Bunker |  | * |  |
| 7.11.2.1 | Imported/Indigenous Coal Bunker |  | * |  |
|  | Bunker water volume | m³ | * |  |
|  | Elevation of top of bunker | m | * |  |
|  | No. of bunker | No. | * |  |
| 7.12 | Dust Collector System |  | * |  |
| 7.12.1 | Electrostatic Precipitator |  | * |  |
|  | Overall size | m x m x m | * |  |
|  | Design gas flow | m3/s | * |  |
|  | No. of fields | No. | * |  |
|  | Thickness of casing | mm | * |  |
|  | Thickness of hopper plate | mm | * |  |
|  | Capacity of hopper | m³ | * |  |
|  | No. of hoppers | No. | * |  |
|  | Collecting electrode : |  | * |  |
|  | - No. |  | * |  |
|  | - Area | m² | * |  |
|  | - Material |  | * |  |
|  | - Spacing | mm | * |  |
|  | Emitting electrode |  | * |  |
|  | - No. |  | * |  |
|  | - Material |  | * |  |
|  | - Spacing |  | * |  |
|  | Overall size | m x m x m | * |  |
|  | Specific collecting area | m²/m³/s | * |  |
|  | Probable supplier |  | * |  |
|  | Height of hopper bottom flange from finished ground floor | m | * |  |
|  | Gas velocity | m/s | * |  |
|  | Residence time | min | * |  |
|  | Aspect ratio |  | * |  |
|  | Inlet dust concentration | gm/Nm3 | * |  |
|  | Outlet dust concentration | mg/Nm3 | * |  |
|  | Holding capacity of hopper |  | * |  |
|  | - First field | m³ | * |  |
|  | - Second field | m³ | * |  |
|  | - Third field | m³ | * |  |
|  | - Fourth Field | m³ | * |  |
|  | Rating of HVR |  | * |  |
|  | - Voltage | kV | * |  |
|  | - Current | mA | * |  |
|  | MCC of ESP in Supplier’s scope | Yes/No | * |  |
| 7.12.2 | Ash Characteristics at Hopper |  | * |  |
|  | Bed Ash Cooler #1 Outlet |  | * |  |
|  | - Ash density | kg/m³ | * |  |
|  | - Ash quantity | kg/h | * |  |
|  | Temperature of ash at outlet | °C | * |  |
|  | No. of outlets | No. | * |  |
|  | Bed Ash Cooler #2 Outlet |  | * |  |
|  | - Ash density | kg/m³ | * |  |
|  | - Ash quantity | kg/h | * |  |
|  | Temperature of ash at outlet | °C | * |  |
|  | No of outlets | No. | * |  |
|  | Economizer |  | * |  |
|  | - Ash density | kg/m³ | * |  |
|  | - Ash quantity | kg/h | * |  |
|  | Temperature of ash at outlet | °C | * |  |
|  | No of outlets | No. | * |  |
|  | Air Heater |  | * |  |
|  | - Ash density | kg/m³ | * |  |
|  | - Ash quantity | kg/h | * |  |
|  | Temperature of ash at outlet | °C | * |  |
|  | No of outlets | No. | * |  |
|  | ESP Field I |  | * |  |
|  | - Ash density | kg/m³ | * |  |
|  | - Ash quantity | kg/h | * |  |
|  | Temperature of ash at outlet | °C | * |  |
|  | No. of outlets | No. | * |  |
|  | ESP Field II |  | * |  |
|  | - Ash density | kg/m³ | * |  |
|  | - Ash quantity | kg/h | * |  |
|  | Temperature of ash at outlet | °C | * |  |
|  | No of outlets | No. | * |  |
|  | ESP Field III |  | * |  |
|  | - Ash density | kg/m³ | * |  |
|  | - Ash quantity | kg/h | * |  |
|  | - Temperature of ash at outlet | °C | * |  |
|  | No. of outlets | No. | * |  |
|  | ESP Field IV |  | * |  |
|  | - Ash density | kg/m³ | * |  |
|  | - Ash quantity | kg/h | * |  |
|  | - Temperature of ash at outlet | °C | * |  |
|  | No. of outlets | No. | * |  |
| 7.13 | Feed Water System |  | * |  |
| 7.13.1 | Feed Pumps (Electro) with motors | % | * |  |
|  | Make |  | * |  |
|  | Type |  | * |  |
|  | Capacity | m³/h | * |  |
|  | Head | kg/cm2 | * |  |
|  | Water temperature | °C | * |  |
|  | NPSH | m | * |  |
|  | Inter stage bleed pressure | kg/cm² | * |  |
|  | Drive motor | kW | * |  |
|  | Recommended drive motor |  | * |  |
|  | - Rating | kW | * |  |
|  | - Speed | rpm | * |  |
| 7.13.2 | Feed Control System Provided |  | * |  |
|  | 100% MCR (Pneumatic) | Yes/No | * |  |
|  | 30% MCR ( pneumatic ) | Yes/No | * |  |
|  | 100% MCR (Pneumatic) | Yes/No | * |  |
| 7.14 | Fans |  | * |  |
| 7.14.1 | Forced Draught Fans (for boiler) | % | * |  |
|  | Type of fan |  | * |  |
|  | Fan duty at MCR: |  | * |  |
|  | - Volume | m³/s | * |  |
|  | - Head | mmWC | * |  |
|  | - bKW | KW | * |  |
|  | Installed parameters : |  | * |  |
|  | - Volume | m³/s | * |  |
|  | - Head | mmWC | * |  |
|  | Working temperature | oC | * |  |
|  | Speed | rpm | * |  |
|  | Coupling |  | * |  |
|  | Recommended drive motor : |  | * |  |
|  | - Rating | kW | * |  |
|  | - Speed | rpm | * |  |
|  | Efficiency of the fan | % | * |  |
|  | VFD included | Yes/No | * |  |
|  | Control damper : |  | * |  |
|  | - Type |  |  |  |
|  | - Actuator |  | * |  |
|  | - Location |  | * |  |
|  | Probable supplier |  | * |  |
| 7.14.2 | Induced Draught Fans (for Boiler) | % | * |  |
|  | Type of fan |  | * |  |
|  | Fan duty at MCR : |  | * |  |
|  | - Volume | m³/s | * |  |
|  | - Head | mmWC | * |  |
|  | - bKW | KW | * |  |
|  | Installed parameters : |  | * |  |
|  | - Capacity | m³/s | * |  |
|  | - Head | mmWC | * |  |
|  | Working temperature | °C | * |  |
|  | Speed | rpm | * |  |
|  | Coupling |  | * |  |
|  | Recommended drive motor : |  | * |  |
|  | - Rating | kW | * |  |
|  | - Speed | rpm | * |  |
|  | Efficiency of the fan | % | * |  |
|  | VFD included | Yes/No | * |  |
|  | Control damper : |  |  |  |
|  | - Type |  | * |  |
|  | - Actuator |  | * |  |
|  | - Location |  | * |  |
|  | Probable supplier |  | * |  |
| 7.14.3 | Primary / Secondary Air Fans | % | * |  |
|  | Type of fan |  | * |  |
|  | Fan duty at MCR : |  | * |  |
|  | - Volume | m³/s | * |  |
|  | - Head | mmWC | * |  |
|  | - bKW | KW | * |  |
|  | Installed parameters : |  | * |  |
|  | - Capacity | m³/s | * |  |
|  | - Head | mmWC | * |  |
|  | Working temperature | °C | * |  |
|  | Speed | rpm | * |  |
|  | Coupling |  | * |  |
|  | Recommended drive motor : |  | * |  |
|  | - Rating | kW | * |  |
|  | - Speed | rpm | * |  |
|  | Efficiency of the fan | % | * |  |
|  | Control damper : |  |  |  |
|  | - Type |  | * |  |
|  | - Actuator |  | * |  |
|  | - Location |  | * |  |
|  | Probable supplier |  | * |  |
| 7.14.4 | Chimney (Common for both Boilers) |  | * |  |
|  | Flue gas to be handled | Nm³/hr | * |  |
|  | Diameter of chimney |  | * |  |
|  | - at base | m | * |  |
|  | - at top | m | * |  |
|  | Height of chimney | m | * |  |
|  | Velocity of the exit of the chimney | m/sec | * |  |
| 7.15 | Soot Blowers |  | * |  |
|  | Type |  | * |  |
|  | Quantity | No. | * |  |
|  | Location and No. | No. | * |  |
|  | Probable Supplier |  | * |  |
| 7.16 | Weight Schedule |  | * |  |
|  | Structures | t | * |  |
|  | Pressure parts | t | * |  |
|  | Non-pressure parts including auxiliaries and ESP | t | * |  |
|  | Insulation and refractory | t | * |  |
|  | Piping | t | * |  |
|  | Total |  | * |  |
| 7.17 | Instrumentation and Controls |  | * |  |
|  | Compressed air requirement : |  | * |  |
|  | - Volume (free air) | m³/h | * |  |
|  | - Pressure | ata | * |  |
|  | Type and Probable supplier for : |  | * |  |
|  | - Control damper actuators |  | * |  |
|  | - Control valves |  | * |  |
|  | - Oxygen analyser |  | * |  |
|  | - Field transmitter |  | * |  |
| 7.18 | Blow Down System |  | * |  |
|  | CBD tank | No. | * |  |
|  | IBD tank | No. | * |  |
|  | Provision of level control | Yes/No | * |  |
|  | Provision of motor operated valve | Yes/No | * |  |
| 7.19 | Chemical Dosing System |  | * |  |
|  | HP Dosing |  | * |  |
|  | - Preparation tank with agitator | No. | * |  |
|  | - No. of pumps | No. | * |  |
|  | - Material of construction |  | * |  |
|  | LP Dosing |  | * |  |
|  | - Preparation tank with agitator | No. | * |  |
|  | - No. of pumps | No. | * |  |
|  | - Material of construction |  | * |  |
| 7.21 | Terminal Points |  | * |  |
|  | For Steam |  | * |  |
|  | - Outlet of main steam stop valve/Non return valve located near to boiler columns. |  | * |  |
|  | - Safety valve outlet piping upto discharge to atmosphere. |  | * |  |
|  | - Outlet of vent pipe upto discharge to atmosphere. |  | * |  |
|  | - Outlet of blow down tank. |  | * |  |
|  | CBD Exhaust at outlet steam stub on tank |  | * |  |
|  | LP steam at inlet of deareator pressure control valve inlet isolation valve. |  | * |  |
|  | For Feed Water |  | * |  |
|  | - DM water at the inlet of deaerator level control station inlet isolation valve, & at one point in Boiler area |  | * |  |
|  | For Condensate |  | * |  |
|  | - At the inlet of De-aerator nozzle |  | * |  |
|  | For Cooling/Service Water |  | * |  |
|  | - Inlet at an agreed single point (one metre away from boiler boundary at ground level). |  | * |  |
|  | - Outlet at nearest drain channel. |  | * |  |
|  | Flue gas |  | * |  |
|  | - Inlet of chimney |  | * |  |
|  | For Combustion Air |  | * |  |
|  | - Inlet to FD fan suction duct work. |  | * |  |
|  | - Inlet to secondary air fan/primary air fan. |  | * |  |
|  | For Ash and Dust |  | * |  |
|  | - Outlet of ash coolers for furnace bottom ash. |  | * |  |
|  | - Outlet pipe work of ash hopper for dust disposable |  | * |  |
|  | For Blowdown and Drains |  | * |  |
|  | - Outlet of blowdown tank to drain. |  | * |  |
|  | For HP and LP Chemical Dosing |  | * |  |
|  | - At an agreed point at ground level . |  | * |  |
|  | For Electrical Power |  | * |  |
|  | - Motor terminal |  | * |  |
|  | For Instrument Air and Plant Air |  | * |  |
|  | - At an agreed single point (1 m away from boiler boundary at ground level). |  | * |  |
| 7.22 | Exclusions |  | * |  |
|  | - RCC chimney |  | * |  |
|  | - Civil foundations |  | * |  |
|  | - Fuel preparation plant |  | * |  |
|  | - Fuels and chemicals |  | * |  |
|  | - Ash and dust disposal system |  | * |  |
|  | - Feed water treatment plant |  | * |  |
|  | - Interconnecting cables (power and earthing) |  | * |  |
|  | - Lighting and socket outlets |  | * |  |
|  | - HT & LT PCC |  | * |  |
|  | - Distribution transformers |  | * |  |
|  | - DCS |  | * |  |
|  | - Registration of the boilers |  | * |  |
|  | - Certain site construction facilities as subsequently defined |  | * |  |

ANNEX II

SCHEDULE OF EQUIPMENT FOR ERECTION AND COMMISSIONING

| Sl. No. | Item |
| --- | --- |
| 1 | ## Steam Drum |
|  | - Fully welded steam drum with manholes |
|  | - Steam drum internals |
|  | - Local water level gauges |
|  | - Remote water level gauge |
| 2 | Furnace |
|  | - Membrane panel water cooled enclosure |
|  | - Access doors/peep holes as required |
|  | - Air nozzles at furnace bottom |
|  | - Various openings/mountings as required |
|  | - Refractory, Refractory holding anchors etc., as required |
| 3 | Superheater |
|  | - Superheater tubes, inlet/outlet headers |
| 4 | Attemperator |
|  | - Direct contact spray type interstage attemperator with spray nozzles and internals |
| 5 | Economiser |
|  | - Economiser tubes/coils |
|  | - Economiser inlet/outlet headers |
|  | - Economiser casing with stiffeners |
|  | - Access door assemblies as required |
|  | - Economiser coils supports |
| 6 | Air Heater (Tubular) |
|  | - Air heater tubes, tube sheets |
|  | - Air heater casing with stiffeners |
|  | - Access door assemblies as required |
| 7 | Buckstays Assembly for Furnace/Boiler |
| 8 | Boiler, Economiser & Air-Heater Supporting Structure – Jubilant scope |
|  | - Supporting structure from ground level (steel execution) |
|  | - Steel galleries/walkways, staircases, handrailings, toe plates, gratings/chequered plates |
|  | - Supporting structure for boiler roof |
|  | - Asbestos sheets for boiler canopy |
|  | - Supporting structure for boiler roof side sheeting |
|  | - Asbestos sheets for boiler roof sides |
|  | - Rust preventive painting (shop) |
|  | - Final painting (site) |
| 9 | Safety Valves |
| 9.1 | Steam Drum |
|  | - Spring loaded mechanical safety valves - 2 Nos. |
|  | - Exhaust piping above roof |
|  | - Drain piping |
| 9.2 | Superheater |
|  | - Spring loaded mechanical safety valve |
|  | - Exhaust piping above roof |
|  | - Drain piping |
|  | - Silencer on safety valve (80 dba @ 10 m distance) |
|  | - Motorised start-up vent valve with silencer |
|  | - Motorised main stop valve |
|  | - Motorised by pass valve |
| 10 | Water System |
| 10.1 | Feed Water (Drum Level Control Station) |
|  | - Feed water (drum level) control valve |
|  | - Isolation/bypass/drain valves |
|  | - Associated piping/fittings/hardware |
| 10.2 | Attemperator Spray Water Control Station |
|  | - Spray water control valve |
|  | - Isolation/bypass valves |
|  | - Associated piping/fittings/hardware |
| 10.3 | Only sampling Pipe work and No Coolers |
|  | - For Boiler feed water sampling |
|  | - For drum water/CBD sampling |
|  | - For saturated steam (from steam drum) |
|  | - For final superheated steam |
| 10.4 | Down Comer and Risers |
| 11 | Soot Blowers – Not Required as per VENDOR |
| 11.1 | Steam Soot Blowers |
|  | - Drive motors |
|  | - Auto sequential control panel |
| 12 | Integral Piping |
| 12.1 | Feed |
|  | - Feed pump discharge form deaerator outlet isolation valve to feed pump suction |
|  | - Feed pump discharge to Feed control station |
|  | - Feed water control station to economiser inlet |
|  | - From attemperator spray water control station to spray water nozzle |
|  | - BFW pumping station to deaerator for minimum flow, blalancing line, and leak of lines upto deaerator. |
|  | - From Economiser outlet to steam drum inlet |
|  | - AII recirculaiton piping involved in the feed water line and associated isolation and regulation valve |
| 12.2 | Main Steam - Upto MSSV/NRV outlet |
| 12.3 | Auxiliary Steam |
|  | - Flash steam from CBD tank outlet to deaerator inlet |
| 12.4 | Vents |
|  | - From individual vent connections on steam drum, main steam line, superheater, economiser upto safe elevation above roof |
|  | - From outlet of safety valves/silencers upto safe elevation above roof |
|  | - From deaerator tank to atmosphere |
| 12.5 | Drain |
|  | - From individual drain points on drums, level gauges/ condensate pots, safety valves, superheater/ economiser headers upto isolation valve on common drain header |
|  | - Common drain header |
|  | - From CBD collection point on steam drum upto outlet of BD valve |
|  | - From common drain header upto BD tank inlet isolation valve |
|  | - Blowdown piping from BD valve to BD tank |
|  | - From BD tank outlet to nearest drain at ground level |
| 12.6 | Cooling Water |
|  | - At one point in Boiler / ESP Area |
| 13 | Draught Plant |
| 13.1 | PA Fans 2 x 125% for boiler |
|  | - Fans with control damper, outlet isolation damper, base frame, foundation bolts/holding down bolts, coupling and hardware |
| 13.2 | ID Fan - 2 x 60% MCR for boiler |
|  | - Fan with suction control dampers outlet isolation dampers, base frame, foundation bolts/holding down bolts, coupling and hardware. |
| 13.3 | FD Fan - 2 x 60% MCR for boiler |
|  | - Fan with control damper, outlet isolation damper, base frame, foundation bolts/holding down bolts, coupling and hardware |
| 13.4 | Ducting and Hoppers |
| 13.4.1 | Ducting |
|  | - PA/SA fan suction |
|  | - From PA/SA fans' discharge upto air heater inlet |
|  | - From air heater outlet upto wind box |
|  | - From furnace outlet upto economiser inlet |
|  | - From economiser outlet to air heater |
|  | - From air heater outlet to ESP inlet |
|  | - From ESP outlet upto ID fan suction damper |
|  | - From ID fan outlet damper to chimney |
|  | - Associated dampers, expansion joints, stiffeners etc. as required |
|  | - Chimney (common for both the boilers) |
| 13.4.2 | Hoppers |
|  | - Hopper below |
|  | - Economiser hoppers |
|  | - Air heater hoppers |
|  | - ESP hoppers |
|  | - Stiffeners, access doors |
|  | - Expansion joints as required |
|  | - Hoppers outlet slide gate |
| 14 | Fuel Feeding System |
| 14.1 | Coal (Imported coal, Indigenous coal,)- Jubilant |
|  | Coal Bunker with Supporting Structure and inside SS lining- Jubilant |
|  | - Isolation gate/Rod gate at outlet of bunker |
|  | - Feed chutes at inlet of fuel feeders |
|  | - Fuel feeders with supporting structure. |
|  | - Fuel feeder discharge chutes |
|  | - Drive electric motors for fuel feeders |
|  | - VFD for fuel feeders |
|  | - Couplings/hardware |
| 14.5 | Start-up fuel firing system with all auxiliaries and accessories |
| 15 | Ash |
| 15.1 | Bed |
|  | - Discharge pipe from bed upto inlet of (slide gates) cooler |
|  | - Bed ash coolers |
| 16 | Castable Refractory/Bricks as required for Boiler |
| 17 | Insulation and Cladding for : |
|  | - Boiler, superheater headers, drums |
|  | - Economiser, air heater |
|  | - Hot air/flue gas ducts |
|  | - Hot water and steam pipelines for Supplier's scope of piping |
| 18 | Instrumentation and Controls |
|  | -DCS & Field instruments as per list of instruments |
|  | - Air filter regulators, junction boxes, I/P converters, as required for above instruments |
|  | - Instrument Air piping From Air filter regulator upto individual consuming point |
|  | - Analyser (only O2) |
|  | -Control room instrumentation |
|  | - Control cabling upto junction box |
| 19 | Boiler Feed Water (BFWP) Pumping Station |
|  | - Electric motor driven BFW pumps with motors |
|  | - Coupling, hardware |
|  | - Base frame, holding down bolts/anchors |
|  | - Inlet/outlet isolation and non return valves |
|  | - Automatic minimum flow recirculation (ARC) valves |
|  | - Piping, mountings/fittings within BFWP station package |
|  | - Mineral wool insulation for package |
|  | - Aluminium cladding |
|  | - Rust preventive painting (shop) |
|  | - Final painting, wherever applicable – By Jubilant |
|  | - Field instrumentation for BFWP package: transmitters, thermocouples pressure/ temperature gauges, Local switches I/P converters etc |
|  | - Control room instrumentation for BFWP station package (DCS) |
|  | - Monorail arrangement and lifting hoist for pump and motor |
| 20 | Chemical Dosing System |
| 20.1 | High pressure (HP) dosing |
|  | - DM WATER piping |
|  | - Dosing tank |
|  | - Dosing pumps |
|  | - Associated piping, valves, mountings, fittings within system |
|  | - Base frame, foundation bolts |
|  | - Piping From HP dosing pumping unit outlet to Inlet of HP dosing connection on steam drum |
| 20.2 | Low Pressure (LP) dosing |
|  | - DM WATER piping |
|  | - Dosing tank |
|  | - Dosing pumps |
|  | - Associated piping, valves, mountings, fittings within system |
|  | - Base frame, foundation bolts |
|  | - Piping From LP dosing pumping unit outlet to Inlet of LP dosing connection on feed line |
| 21 | Blow Down Tanks |
| 21.1 | Continuous blow down (CBD) tank (Common for both the boilers) |
|  | - Tank with associated stubs, nozzles, flanges, manhole |
|  | assembly etc. |
|  | - Mineral wool insulation |
|  | - Aluminium cladding |
|  | - Supporting structure |
|  | - Field instrumentation |
|  | - Control room instrumentation (DCS). |
|  | - Rust preventive painting (shop) |
|  | - Final painting (site) – By Jubilant |
| 21.2 | Intermittent blow down tank (IBD) |
|  | - Tank with Associated stubs, nozzles, flanges, manhole assembly etc |
|  | - Mineral wool insulation |
|  | - Aluminium cladding |
|  | - Supporting structure |
|  | - Field instrumentation |
|  | - Control room instrumentation. |
|  | - Rust preventive painting (shop) |
|  | - Final painting (site) – By Jubilant |
| 22 | Electrostatic Precipitator |
|  | - Inlet/outlet transition pieces |
|  | - Inlet/outlet isolation dampers |
|  | - ESP inlet expansion bellow |
|  | - ESP outlet expansion bellow |
|  | - Electrostatic precipitator complete with discharge, collecting electrodes, rapping devices, transformer rectifier sets, insulators |
|  | - ESP control panel, switchgear |
|  | - Power and control cables From MCC outlet terminal upto the ESP control panel terminals and earthing system |
|  | - Outer casing on ESP duly covered by insulation and cladding |
|  | - Ash collection hoppers |
|  | - Rotary air lock feeders for hoppers |
|  | - Hopper heating system complete with control panel, power and control cabling, switchgear, thermostats etc |
|  | - Complete supporting structure from ground level, including operating platforms, staircases, handrails and toe plates |
|  | - Rust preventive painting |
|  | - Final painting (site) by Jubilant |
| 23 | SWAS for pH and conductives of feed water, drum water, saturated steam and superheater steam- SWAS by Jubilant – Connectivity and trial by Vendor |
| 24 | O2 analyser - On line |
| 25 | Chimney - Jubilant |
| 26 | Civil |
|  | - Basic engineering for foundation, design and load details etc.equipmenmt Load Data , GA Drawings , plan , elevation |
| 27 | Erection and Commissioning |
|  | - Erection and commissioning on turn key basis of VENDOR supplied items |
|  | - Supervision of erection and commissioning of the items even if in Jubilant scope |

Performance Parameters

|  |  |  | # Coal |
| --- | --- | --- | --- |
| 1 | Steam output of the Boiler for 24 Hrs & 365 days in a Year | TPH | 65 |
| 2 | Steam pressure at Boiler outlet | Ata | 80 |
| 3 | Steam temperature at Boiler Outlet | 0C | 515± 5 |
| 4 | Steam temperature Range | % | 60- 110 |
| 5 | Boiler Thermal Efficiency | % |  |
| 5.1 | Boiler Efficiency with Indian Coal of GCV 2997 Kcal/Kg | % |  |
| 5.2 | Boiler Efficiency with Indian Coal of GCV 3800 Kcal / Kg | % |  |
| 5.3 | Boiler Efficiency with Imported Coal of GCV 5700 Kcal / Kg | % |  |
| 6 | Aux. Power consumption of Boiler & ESP |  |  |
| 6.1 | With VFD | KW |  |
| 6.2 | Without VFD | KW |  |
| 7 | Outlet Dust Emission Level | Mg/Nm3 |  |
| 8 | Deaerator Performance |  |  |
| 8.1 | Temp at outlet of deaerator | 0C |  |
| 8.2 | Oxygen content in water at the outlet of deaerator | ppm |  |
| 9 | Steam Purity |  |  |
| 9.1 | Thermal Conductivity at 25 0C , max | Ms/cm | 0.2 |
| 9.2 | Silica | ppm | 0.02 |
| 9.3 | Dryness factor | % | * |
| 10 | Noise Level | dBA | 85 |
| 11 | Temp difference between Insulation surface & ambient | 0C | 20 |
| 12 | Efficiency Calculations |  | ASME PTC 4.1 |

The Break up of the power is to be provided by Vendor as below:

| SL. NO. | DESCRIPTION | QUANTITY |  |  | INSTALLED MOTOR CAPACITY |  | POWER CONSUM-PTION AT EQUIPMENT SHAFT DURING 100% MCR WITHOUT CONSIDERING MOTOR EFFICIENCY AND CABLE LOSSES (KW) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Total | Work -ing | Stand by | KW / Unit | Total |  |
| 01. | FD Fan motor |  |  |  |  |  |  |
| 02. | ID Fan motor |  |  |  |  |  |  |
| 03. | PA Fan |  |  |  |  |  |  |
| 04. | Boiler feed pumps |  |  |  |  |  |  |
| 05. | Drag chain feeders |  |  |  |  |  |  |
| 06. | LP dosing pumps |  |  |  |  |  |  |
| 07. | HP dosing pumps |  |  |  |  |  |  |
| 08. | Motorised agitator |  |  |  |  |  |  |
| 09. | ESP |  |  |  |  |  |  |
|  | TOTAL - WITH VFD - WITHOUT VFD |  |  |  |  |  |  |

# Penalties

In case there is delay in delivery beyond the schedule herein stated, penalty @ 0.5 % of the order Valve shall be deducted from Vendor payment for each full week of delay subjected to the maximum of 10% of the order value.

The following shall be the liquidated damages payable from the guaranteed figures furnish by Vendor:

- Rs 80,000.00 for every one (1) Kilowatt increases over the guaranteed value at 100% MCR Condition.

- Rs 5,00,000.00 for every 0.1% decrease in Boiler Efficiency over the guaranteed figure.

- Rs 10,00,000.00 for every 2% reduction in steam flow over the guaranteed value.

- Rs 5,00,000.00 for every 2 oC reduction in steam temperature at SH Outlet

Additional Points to be incorporated:

Electrical Points

1.The Boiler &  ESP MCC shall be LT. The MCC’s shall be as per Jubilant Specifications.

2. The following parameters shall be considered while designing the LT System

2.1 Design Temp – 50 Deg C.

2.2 Supply voltage variation +/- 10 %, Cycle +/- 5 % ,cumulative 10 %

2.3 Motors EFF1, class F insulation with temp rise of 75 Deg c. MCC suitable for 3ph ,4 wire , 415 v, 50 KA fault level.

2.4Degree of Protection IP-55

3. The Boiler & ESP MCC shall be located in the existing MCC Room

4.ESP MCC & TR sets shall have provision to hook up with DCS for monitoring purpose.

5. Digital Energy meters shall be provided for ESP MCC & hook up to DCS through soft acquisition protocol (RS485). All Major drive shall have remote operation facility through DCS( Preferred make –schneider). All MCC incomer shall have energy meters with RS 485 comm.Protocol for data acquisition on DCS

6. All motors above 200 KW shall be HT

7. In MCC all Siemens / Schneider make components shall be used.

Instrumentation Points

1.VENDOR shall supply  bottom mounted bed temp thermo-couples as against front mounted bottom thermocouples.

2. The design of the thermowell MOC shall be 1.5 times more than the operating range.

3.Thermowell shall be screwed / threaded for connections down below instead of welded to DP plate. Jubilant shall provide the drawing for the same.

4.Jubilant ahs asked for higher MP MOC for outer sheath and elements of thermocouples than that of thermowells. VENDOR shall take care for higher MP MOC for outer sheath and elements of thermocouples than that of thermowells during detailed engineering phase.

5. The bed height measurement shall be based on air box pressure and remote signal also. A flush mounted local gauges for all the six compartments to be provided at burner floor instead of local mounted gauges. VENDOR shall provide the draught gauges in addition to draft transmitter for air box draught measurement.

6. VENDOR shall provide the control logic for DCS & FAT shall be attended by VENDOR automation engineer for correctness of programmed logics.

7. All the temp elements shall be RTD’S & Thermo-couples as per the application suitability. All RTD for motor/ fan/pump bearing shall be headless type with 10 mtr Teflon insulated cable and tinned metal screen. All temp elements shall be with thermowell. Thermowells for flue gas temp should have extra strength to prevent problem of sagging/bending.

8. All the temp elements i.e. RTD & thermocouples shall be duplex type.

9. VENDOR shall provide flow switch in sealing water lines of BFW Pump.

10. VENDOR shall provide one pressure transmitter on Instt. Air Header.

11. All Control valves and RPC’s shall be provided with the Smart Valve Positioner, position feed back transmitter and PNP type proximity type switches for close limit with desired level under fail safe operation.

12. VENDOR shall provide optical & galvanic isolation for all field analog signals reporting to DCS shall be 24 V/ 4- 20 Ma.

13. All transmitters shall be smart with HART protocol of latest version. DP transmitters must be provided with 5 way SS316 manifold and pressure Transmitters with SS316 Isolation needle valve. Main isolating valve to be provided at all tapping points especially for feed water and steam circuit.

14. The steam flow meter shall be Flow Nozzle type.

15.VENDOR shall provide 1 no additional Furnace pressure transmitter.

16. VENDOR shall provide level transmitter instead of Level switch for de-aerator low level measurement.

17.VENDOR shall provide additional 1 no Steam Drum Pressure Transmitter.

18. The draft transmitter at Furnace and before economiser shall be used for pressure drop measurement.

19. For solenoid operated instt , VENDOR shall meet the following requirements.

19.1 All open/ close valve should have open and close limit proximity switches for status on DCS with local open/ close indication.

19.2 Pneumatic actuators shall be die cast Aluminium with suitability for open installation of Elomatic or Amri/Neles make.

19.3 All electronic and electrical devices such as proximity, solenoid should be of 24 V dc with IP67 compliance.

19.4 All gang-mounted solenoids should be suitably grouped for different circuits with facility of online repair and maintenance without affecting functioning of others.

19.5 MOC of solenoid should be corrosion resistant.

19.6 All relays to be used with proximity should be of solid state type mounted in safe area i.e. CR.

19.7 All SOPCs should be with supplied with reed switches for open-close status to DCS with local LED indication . Make; FESTO/SMC/SHCENIDER

20. Vendor shall provide Motorised valves (start up vent only) and actuators with position feedback to DCS with  set of (2NO+2NC) potential free contacts for Open, Close & torque limit contacts and LPBS having start, stop and emergency push buttons.  Starter shall be located in the MCC which is under JOL scope. Actuator should have IP67 protection. Make ; Auma / Rotork.

21. VENDOR shall supply ESP TRCC control system shall be microprocessor based controller with RS 485 connectivity facility to DCS for monitoring purpose with following features –

Remote start-stop and set point from DCS.

Remote monitoring signals i.e. 4-20mA for kV and mA to DCS.

All panel control wiring should be with tinned copper conductors only.

All electronics should have conformal coating for G3 compliance as per ISO 71.04.

22. VENDOR  will provide pressure transmitter for measurement of pent house pressure through purge air blower and RTD for temperature to DCS.

23. VENDOR shall supply high-level switches for ESP, APH, Economizer, ash hoppers.

24. VENDOR will provide the fittings and impulse piping of the following specifications

SS316 piping for Instrument air to AIR HEADERS.

MOC of air header X8 and 1/2'’ ball each distribution point should be SS316.

Air header should be provided with main isolating and drain valve.

A pressure gauge must be provided at all air headers.

½’’ NPT fittings and 12mm OD seamless SS316 impulse pipes must be used for air distribution to individual instrument.

FRL to be provided at all pneumatic instrument.

Metal alloy Impulse piping with IBR grade isolating valves to be used for impulse piping for transmitter for steam and feed-water circuit.

No where copper tubing or cu/brass fittings are to be used.

All steam line pressure gauges are to be provided with SS or alloy syphon and snubber.

25. VENDOR to supply separate junction box for AI, A0, DI, D0, RTD & thermocouple inputs.   Also note that we have considered junction boxes of die cast aluminium material of construction.

26. VENDOR shall supply  VFDs with –

Panel mounting/installation type.

Panel should be of RITTAL or better make

Panel should have sufficient number of cooling air circulation fans and detachable type cartridge filters, tube light with door switch.

Each VFD should have isolating HRC fuses or MCBs in addition to common MCCB.

Panel should be duly wired with ferruled terminal using tinned copper conductor.

All indication should be LED based.

Each drive should have local-remote selection switch, On-Off and Emergency P.B. and local display and keypad for configuration and control.

Each VFD should give isolated output of 4-20mA for True RPM,KW and must accept remote analogue set point and digital IOs for remote start, stop command and run status.

27. VENDOR shall supply all the electronics DCS, PLC,VFDs,CONTROLLERS, ANALYSER etc should have strict compliance to –Conformal coating for G3 as per ISA 71.04 &IP67 for open installation.

28. All local monitoring instruments should have –MOC SS316/corrosion resistant for pressure and temperature gauges with internal of SS304

29. VENDOR shall provide all necessary documents for I & C like Master I/O list with instrument details, valve-sizing calculations, P&ID, instrument specification sheet, instrument hook diagram,cable termination schedule, cable tray routing with JB location diagram, process control and inter-lock logics and Control system flow diagram during the detailed engineering stage.

30. Boiler start up & shut down, interlocks & protection logics shall be submitted during detailed engineering stage by VENDOR.

# LIST OF APPROVED SUB-VENDORS FOR BROUGHT  ITEMS

MECHANICAL

- FANS

#	a	VENDOR

2.	FEED PUMPS

- KSB

- SULZER

3.	IBR VALVES

- KSB

- BHEL

- AUDCO

4.	BLOW DOWN VALVE

- BHARAT HEAVY ELECTRICALS LTD

- AUDCO

C.   LEVCON

5.	BUTTERFLY VALVES

- AUDCO

b.   INTER VALVE

6.CONTROL VALVES

- DRESSER MASONEILAN

- INSTRUMENTATION LIMITED

- MIL CONTROLS

- FISHER XOMOX

- VALFLO

- FORBES MARSHALL

- FOURESS

7.	PRDS

- CHEMTROL / BTG

- YARWAY

- ARCA

- FOURESS

- IL

- MIL

- VENDOR (DESUPERHEATER)

8.BELLOWS (METALLIC)

a.   VENDOR

9.CENTRIFUGAL PUMPS

- KIRLOSKAR

- KSB

10.PUMPS

- AKAY

- SULZER

- KIRLOSKAR

11.RELIEF & SAFETY VALVES

- AUDCO INDIA LTD

- BHARAT HEAVY ELECTRICALS LTD

- TYCO SANMAR

12.SPRING HANGERS

- BHARAT HEAVY ELECTRICALS LTD

- SARATHI

13.LUBE OIL SYSTEM

- SOUTHERN LUBRICANTS

- ALFA LAVAL

- GRAND PRIX

14.SOOT BLOWERS

- BHEL

- SITSON

- RR Techno Mech

15.	FABRIC EXPANSION JOINTS

- KELD ELLENTOFT

- BACHMANN

- GBM

16.	DIRECT WATER LEVEL GUAGE

- YARWAY

- CHEMTROL

- LEVCON

17.	MINERAL WOOL INSULATION

- MIN WOOL

- LLOYD ROCK FIBRES

- ROCK WOOL INDUSTRIES

- ROCKWOOL INDIA (I) LIMITED

18.	ALUMINIUM CLADDING

- BALCO

- INDAL

- HINDALCO

19.	REFRACTORY & INSULATING BRICKS

- R.V. REFRACTORIES

- ACC

- CAST WELL INDUSTRIES

- BASKAR REFRACTORY

- DALMIA REFRACTORY

ELECTRICAL

1.	VARIABLE FREQUENCY DRIVE

a)	L&T

b)	SIEMENS

- ALLEN BRADLEY

- AMTECH

- ABB

- HIREL

2.	MOTOR CONTROL CENTRES

a)	SIEMENS

- L&T

- GE POWER

- ADVANCE CONTROLS

3.	XLPE CABLE TERMINATION KITS

a)	CCI

- M-SEAL

- REYCHEM

- Birla 3-M

4.	MOTORS

  - BHEL

  - SIEMENS

  - BHARAT BIJELE

### 5.	POWER & CONTROL CABLES

a)	CABLE CORPORATION OF INDIA

b)	UCL

- NICCO

- FORT CLOSTER

- SPECIAL CABLES

- TCL

- RPG

- POLYCABS

- UNIVERSAL

### 6.	TRANSDUCERS

a)	ABB

b)	AE

c)	SIEMENS

7.	LT SWITCHGEAR COMPONENTS

a)	SIEMENS

b)	L&T

c)	GE - POWER

INSTRUMENTATION

1.	AIR FILTER REGULATOR

  - PLACKA

  - SHAVO NORGEN (INDIA) PVT LTD

2.	FLOW NOZZLE / ORIFICE

  - JN MARSHALL

  - MICROPRECISION PRODUCTS

  - IL (PALGHAT)

#         d)         VENDOR (ORIFICE)

3.	INDICATING METERS

  - AE

  - RISHAB

4.	INSTRUMENT CABLES

a)	TCL

b)	PARAMOUNT

c)	CORDS

d)	DELTON

e)	THERMOPADS

f)	ASSOCIATED

5.	INSTRUMENT TRANSFORMERS

a)	AE

b)	GEC

c)	KAPPA

6.	I/P CONVERTORS

a)	ABB

b)	ROSEMOUNT

c)	BELLS

7.	LEVEL GAUGES

a)	LEVCON INSTRUMENTS PVT LTD

b)	V. AUTOMAT

8.	OXYGEN ANALYSERS

a)	ROSEMOUNT

b)	Yokogawa

c)	ABB

9.	POWER CYLINDERS

a)	FISHER

b)	INSTRUMENTATION LTD

c)	KELTRON

d)	BELLS

#

10.	PRESSURE & DP TRANSMITTER

a)	ABB

b)	ROSEMOUNT

c)	TATA HONEY WELL

d)	FUJI

e)	YBL

11.	PRESSURE GAUGES

#	a)MASS PRECESSION

#	b)WARRE

c)	H. GURU

#	d)WIKA

12.	PRESSURE SWTICH & TEMPERATURE SWITCHES

- INDFOSS

- SWITZER

13.	RTD AND THERMO COUPLES

- GENERAL INSTRUMENTS

- PYROELECTRIC

- DETRIV

- PYROTECH

e)	NUTECH

f)	TEMPSONS

- SOLENOID VALVES

- ASCO

- ROTEX

- HERION

- NUCON

15.	 TEMPERATURE GAUGES

a)	WAREE

b)	MASS PRECESSION

c)	GIC

d)	PYROELECTRIC

e)	H. GURU

16.	ALARM ANNUCIATORS

- MASSIBUS

- PROCON

17.	 PLC

- ALLEN BRADELY

- SIEMENS

- TATA HONEYWELL

- ABB

### 18.	REMOTE PANEL MOUNTED INDICATORS

- BELLS CONTROLS LIMITED

- YOKOGAWA

19.      SINGLE LOOP CONTROLLERS

- BELLS CONTROLS

- SIEMENS LTD

- TATA HONEYWELL LTD

- YOKOGA BLUESTAR LTD

20.	SWAS

a)	HACK ANALYSER

b)	FORBES MARSHAL

c)	FISHER ROSEMOMENT

d)	ABB