Quotation on main parts of the one 60mva substation

| Item | Name | Specification | Unit | Quantity | Unit Price in USD | Remark |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Power transformer | SZ10-60000/132 | unit | 1 | 859,047.62 |  |
| 2 | High voltage switchgear | LW30-145/3150-40 | Unit | 1 | 37,539.68 | Taikai |
| 3 | 145KV surge arrester |  | Piece | 1 | 2,444.44 | Taikai |
| 4 | Medium voltage switchgear | LW8-35/1250 |  | 1 | 20,952.38 | Taikai |
| 5 | 36KV disconnectors |  |  |  | 3,666.67 |  |
| 6 | 36KV voltage transformer |  |  | 1 | 4,015.87 | Taikai |
| 7 | 300KVA grounding transformer |  |  | 1 | 68,095.24 | Taikai |
| 8 | Auxiliary |  | Set | 1 | 13,968.25 | Taikai |
| 9 | Control cubicle |  | Set | 1 | 62,857.14 | Taikai |
| 10 | 36KV surge arrester |  |  | 1 | 1,047.62 | Taikai |
| 11 | Expulsion fuse cutout |  |  | 1 | 2,619.05 | Taikai |
| 12 | trailer |  |  | 1 | 11,873.02 | Taikai |
| 13 | Spares as required in buyer’s schedule |  | set | 1 | 8,380.95 | Taikai |
|  | Total |  |  |  | 1,096,507.94 |  |

Remarks:

- Quotation is on FOB Shanghai, China.

- Validity: one months after 27th, Aug. 2008.

- Delivery: 3-4 months after contract effectiveness.

- Usd: Chinese Currency ratio is based on 6.7, if changed, USD quotation to be adjusted accordingly.

- Transformer technical specification:

| Item | Name | Specification | Unit | Quantity | Remark |
| --- | --- | --- | --- | --- | --- |
| 1 | 110kV Transformer main body | SZ10-60000/132 | unit | 1 | Taikai |
| 2 | Bushing | BRDLW-154/630-4 |  | 3 | Xian |
| 3 |  | BRDLW-72.5/630-4 |  | 1 | Xian |
| 4 |  | BDW-20/3000 |  | 3 | Heibei |
| 5 |  | BJL-10/50 |  | 2 | Heibei |
| 6 | Switch | CMIII-350Y/110B-10193W |  | 1 | Shanghai |
| 7 | Protection | QJ4-80A |  | 1 |  |
| 8 |  | YSF9-55/130DKJ |  | 1 |  |
| 9 |  | BWY-803AJ/XMT-22B |  | 2 | Dalian jinzhou |
| 10 |  | Current transformer |  | 13 | Nanjing Zhida |
| 11 | Cooling system | PC2600(2200)-30(2)/520 |  | 16 | Heibei |
| 12 |  | End cubic |  | 1 | Taikai |
| 13 | Oil cubicle | Corrugated cubicle |  | 1 | Shengyang jiahua |
| 14 | transportation |  |  |  | To Shanghai Port |

Technical Specification on main systems in the substation

| Item | Description | Units | Required | Guaranteed |
| --- | --- | --- | --- | --- |
| A | Power transformer |  |  |  |
| 1 | Manufacture |  | Specify |  |
| 1.1 | Country of origin |  | Specify | TaiKai |
| 1.2 | Type |  | Oil immersed | Oil immersed |
| 1.3 | No. of phase/winding |  | Three phase with 2 windings | Three phase with 2 windings |
| 2.0 | Rated data and characteristic |  |  |  |
| 2.1 | Rated power –primary/secondary | MVA | 60 | 60 |
| 2.2 | Cooling |  | ONAN/ONAF | ONAN/ONAF |
| 2.3 | Rated voltage -HV winding -LV winding | kV kV | 132 33 | 132 33 |
| 2.4 | Tap changer Manufacture Country of origin Model Type On load tap changer location Regulating range |  | OLTC Specify specify CFVV HV neutral 132kV ±8×1.25% Rated power on all taps | OLTC TaiKai China SF10 HV neutral 132kV ±8×1.25% Rated power on all taps |
| 2.5 | Frequency | HZ | 50 | 50 |
| 2.6 | Connection of the three phase-windings |  | Ynd11 | Ynd11 |
| 2.7 | Rated current at ONAF rated power and rated voltage tap -HV winding -LV winding | A | 262 1050 | 262 1050 |
| 2.8 | No-load current trough -HV winding -LV winding | A | - | - |
| 2.9 | Short circuit capacity HV system Short circuit capacity LV system |  | 7000MVA 1000MVA | 7000MVA 1000MVA |
| 2.91 | Direct impendence at nominimal voltage tap:HV/LV | % | 10.2 | 10.2 |
| 2.9.2 | Direct impendence at minimum voltage tap: |  | 10.6 | 10.6 |

Section VL Schedule of Requirements

| TECHNICAL DATA SCHEDULE 60MVA,132/33KV MOBILE SUBSTATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| ITEM | DESCRIPTION | UNITS | REQUIRED | GUARANTEED |
| 2.13 | Highest voltage for equipment: -HV winding -LV winding | KV KV | 145 36 | 145 36 |
| 2.14 | Rated insulation level: |  |  |  |
| 2.14.1 | Short time low frequency applied voltage withstand: -HV winding-line terminal -LV winding-line terminal -HV neutral-graded insulation -control wiring | KV RMS KV RMS KV RMS KV RMS | 275 70 70 2.0 | 275 70 70 2.0 |
| 2.14.2 | Full Wave Impulse-Basic impulse level: -HV winding-line terminal -LV winding-line terminal -HV neutral graded insulation | KV (peak) KV (peak) KV (peak) | 650 170 170 | 650 170 170 |
| 2.15 | Temperature rise limits at maximum power Output at ONAN and ONAF rating and at lowest voltage tap and corresponding voltage: -Ambient temperature -Top oil temperature rise -Average winding temperature rise - Temperature class | ℃ ℃ ℃ | 45 55 65 A | 45 55 65 A |
| 2.16 | Permissible overload in emergency cases: -permanent permissible overload based on Highest winding temperature which exceeds by 5℃ the guaranteed limit -permanent permissible overvoltage based on the maximum top oil temperature which exceeds by 5℃ the guaranteed limit at rated power(in % of the rated voltage) | MVA % | Specify Specify |  |
| 2.17 | Oil; -manufacturer -type -data sheet attached |  | PCB prohibited Specify NYNAS Yes | PCB prohibited Kelamayi NYNAS Yes |
| 2.18 | Bushing |  |  |  |
| 2.18.1 | HV bushings: -class -manufacturer -type designation -rated current -short circuit withstand -basic insulation level -power frequency withstand for 1 minute -creepage distance | KV A KA RMS KV (peak) KV RMS mm | 145 Specify Specify Specify Specify 650 275 31mm/kv | 145 Specify Specify Specify Specify 650 275 31mm/kv |
| 2.18.2 | LV bushings: - class - manufacturer - type designation - rated current | kV - - A | 36 Specify Specify Specify | 36 Specify Specify Specify |

96                                            Section VI. Schedule of Requirements

| TECHNICAL DATA SCHEDULE 60MVA, 132/33 kV MOBILE SUBSTATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| ITEM | DESCRIPTION | UNITS | REQUIRED | GUARANTEED |
|  | - ONAF maximum rating | dB(A) | 78 max |  |
| 2.21 | Radio Interference Voltage at 0.5 MHz as per IEC 694 | μV | 2500 max | 2500 max |
| 3.0 | Weights and dimensions |  |  |  |
| 3.1 | Total weight of transformer, equipped for service | Kg - |  | 87000 |
| 3.2 | Weight: - oil - core and coil assembling - tank and accessories - net copper - net core steel | kg kg kg kg kg | Specify Specify Specify Specify Specify | 21000 21979 |
| 3.3 | Maximum shipping weight (heaviest item) | Kg | Specify | 65000 |
| 3.4 | Height from foundation to: - highest point of HV bushing -highest point of tank - -highest point of conservator tank -highest point of lifting hook to remove core and coil assembly | mm mm mm mm | Specify Specify Specify Specify |  |
| 3.5 | Outline dimensions: - length - width | mm mm | Specify Specify |  |
| 3.6 | Layout drawing |  | To be enclosed with bid | To be enclosed with bid |
| 3.7 | Maximum shipping dimensions of tank: - outside height - outside width - outside length | mm mm mm | Specify Specify Specify | 6570 2450 3640 |
| 3.8 | Transportation drawing |  | To be enclosed with bid | To be enclosed with bid |
| 4.0 | On-load tap changer |  |  |  |
| 4.1 | Manufacturer |  | Specify |  |
| 4.2 | Type |  | Specify |  |
| 4.3 | Rated current | A | Specify |  |
| 4.4 | Number of steps | - | 17 |  |
| 4.5 | Short circuit withstand | kA RMS | Specify |  |
| 4.6 | BIL to ground through the regulating coil | kV (peak) | Specify |  |
| 4.7 | Power frequency withstand voltage for 1 minute through the regulating coil | kV RMS | Specify |  |
| 4.8 | Tap transition device | - | Resistance type |  |
| 4.9 | Parallel automatic controller - | - | Master-follower |  |

- Section VI. Schedule of Requirements

| TECHNICAL DATA SCHEDULE 60MVA, 132/33 kV MOBILE SUBSTATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| ITEM | DESCRIPTION | UNITS | REQUIRED | GUARANTEED |
| 6.4 | Tap changer - | - | Transv. Axis | Transv. Axis |
| 6.5 | Control cabinet - | - | Specify |  |
|  | 6.6 Radiators - Specify |  |  |  |
| 6.7 | Terminal block connection drawing - | - | drawings to be enclosed | drawings to be enclosed |
| 7.0 | Standards |  |  |  |
| 7.1 | Manufacturing - | - | IEC 60044 IEC 60076 IEC 60137 IEC 60214 IEC 60529 IEC 60815 IEC 60947 NEMA TR-1 | IEC 60044 IEC 60076 IEC 60137 IEC 60214 IEC 60529 IEC 60815 IEC 60947 NEMA TR-1 |
| 7.2 | Quality assurance - | - | ISO 9001 | ISO 9001 |
| 8 | Auxiliary supply voltages |  |  |  |
| 8.1 | OLTC motor and fans, at 50Hz | Vac | 415 | 415 |
| 8.2 | OLTC & cooling control circuits | Vac | 240 | 240 |
| 8.3 | Heaters and lights | Vac | 240 | 240 |
| 8.4 | Relays & instruments | Vdc | 110 | 110 |
| 9 | High voltage switchgear – | - | 132kV | 145kV |
| 9.1 | Insulation Type |  | Air or Gas | Gas |
| 9.2 | Rated voltage / maximum voltage | kV | 132 / 145 | 132 / 145 |
| 9.3 | Power frequency withstand voltage(1/ min | kV (rms) | 275 | 275 |
| 9.4 | Lightening impulse withstand voltage | kV(peak) | 650 | 650 |
| 9.6 | Rated current | A | 2500 | 3150 |
| 9.7 | Rated short - time withstand current (1sec) | kA | 40 | 40 |
| 9.8 | Current transformer ratio -Metering class ( core 1) -burden -Security factor -Protection class ( core 2) -burden -Accuracy limit factor | A | 300-600-1200/1 0.2 20 <10 5p 20 20 | 300-600-1200/1 0.2 20 <10 5p 20 20 |
| 9.9 | Design pressure of circuit breaker enclosure-Rated circuit breaker operating sequence - Stored switching sequence -Rated current of circuit breaker -Rated short time withstand current -Rated DC voltage -Rated making current | kPa A kA V kA | 800 O-0.3s-CO-1min- CO O – CO 3150 40 110 100 | 800 O-0.3s-CO-1min- CO O – CO 3150 40 110 100 |
| 9.10 | Routine test pressure | kPa | 1200 | 1200 |

100                         Section VI. Schedule of Requirements

| TECHNICAL DATA SCHEDULE 60MVA, 132/33 kV MOBILE SUBSTATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| ITEM | DESCRIPTI ON | UNITS | REQUIRED | GUARANTEED |
|  | -Rated operating sequence acc to IEC -Rated DC voltage 110 -Auxiliary contacts - -Power frequency -Impulse | V Kv kV | O-0.3s-CO-15s-CO 110 4NO + 6 NC 70 170 | O-0.3s-CO-15s-CO 110 4NO + 6 NC 70 170 |
| 11.2 | 36kV Disconnector -Manufacturer - -Country of origin - -Type - -Rated current -Power frequency withstand across isolating distance -Lightning impulse withstand voltage (1sec) -Rated peak current -Short circuit withstand at 1sec | A kV kV kA kA | Specify Specify Outdoor/Indoor 1250 75 170 78 31.5 | TaiKai China Outdoor/Indoor 1250 75 170 78 31.5 |
| 11.3 | 36kV voltage transformer -Manufacturer - -Country of origin - -Type - -Thermal capacity -Rated output -accuracy class -Voltage factor/time -Voltage ratio One minute power frequency withstand voltage on: - Primary winding - Secondary winding - Ratted voltage - insulation material / color | VA VA Class kV kV kV | Specify Specify Outdoor/Indoor 1500 20 3p 1.5 / 30s 33000/√3:110/√3: 110/√3 70 2.5 33 Porcelain / brown | Outdoor/Indoor 1500 20 3p 1.5 / 30s 33000/√3:110/√3: 110/√3 70 2.5 33 Porcelain / brown |
| 11.4 | 300kVA Grounding Transformer - Rated power - Primary Rated voltage - Primary connection - Vector group -Rated insulation level HV side -Rated insulation level LV side -Secondary connection -Secondary rated voltage, no load -Insulation class | kVA kV kV kV V | 300 33, 2x2.5% Zigzag Znyn 36/70/170 3 Star + neutral 415/240 Specify | 300 33, 2x2.5% Zigzag Znyn 36/70/170 3 Star + neutral 415/240 Specify |

- Section VI. Schedule of Requirements

| TECHNICAL DATA SCHEDULE 60MVA, 132/33 kV MOBILE SUBSTATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| ITEM | DESCRIPTION | UNITS | REQUIRED | GUARANTEED |
| 12.2 | - Load on King Pin (approx) - Axels - Dimensions (approx) | Ton Qty m | 18 6 (3 steerable) (LxWxH) 17x3.5x4.5 | 18 6 (3 steerable) (LxWxH) 17x3.5x4.5 |
| 12.3 | Auxiliary - 24VDC connection to 24VDC system of prime mover - spirit level on trailer |  | Specify | Specify |
| 12.4 | - Brakes | Qty | 2 pneumatic brake systems | 2 pneumatic brake systems |
| 13.0 | Control Cubicle: | No. | 1 | 1 |
| 13.1 | General Consists of two compartments, one contains relays, control equipment, AC/DC panel and the other one contains the batteries. The floor of the building shall be covered with rubber sheet. |  |  |  |
| 13.2 | Walls and roof: This shall be of sandwitch construction using plastic coated aluzink sheet on both sides of an polyurethane insulation layer. Total thickness not less than 60mm. The roof shall be covered with rubber sheet. |  |  |  |
| 13.3 | Lighting: Both compartments shall be illuminated with compact fluorescent lamps (CFL). |  |  |  |
| 13.4 | Heating: The rooms shall be installed with panel type, adjustable temperature regulator. |  |  |  |
| 13.5 | Ventilation: The cubicle shall be equipped with an air- conditioning unit with adequate cooling o capacity for ambient temperature of 45 C. The cubicle shall be installed with ventilators capable of keeping dust outside the room. |  |  |  |