Rated Voltage up to 0.6/1kV PVC Insulated Power Cable

The product is used for electrical power transmission and distribution systems, operating at A.C. rated voltage (Uo/U) up to 0.6/1kV.

1.  Manufacturing Standards:

The standards are GB/T12706-2002, IEC60502.

2.  Application requirements:

Max. permissive operating temperature of conductor in long-term is 70℃.

- The conductor short-circuit temperature shall not exceed 160℃ (duration no more than 5s).

- The ambient temperature shall not be lower than 0℃ during installation. The minimum bending radius shall be as follows:

For single core cable: 20（D＋d）±5％mm

For multi-core cable: 15（D＋d）±5％mm

where:

D is the actual outer diameter of the cable        mm;

d is the actual outer diameter of the conductor)    mm.

- Type and Specification:

a. Refer to table 1 about the type:

Table 1

| Type |  | Name |
| --- | --- | --- |
| VV | VLV | PVC insulated PVC sheathed power cable |
| VY | VLY | PVC insulated PE sheathed power cable |
| VV22 | VLV22 | PVC insulated PVC sheathed steel-tape armored power cable |
| VV23 | VLV23 | PVC insulated PE sheathed steel-tape armored power cable |
| VV32 | VLV32 | PVC insulated PVC sheathed thin steel-wire armored power cable |
| VV33 | VLV33 | PVC insulated PE sheathed thin steel-wire armored power cable |
| VV42 | VLV42 | PVC insulated PVC sheathed thick steel-wire armored power cable |
| VV43 | VLV43 | PVC insulated PE sheathed thick steel-wire armored power cable |

Note:

Our company can also produce flame-retardant, fire-resistant, anti-termite, low smoke and non-halogen cables respectively according to the requirements of customers.

for flame-retardant cables, the writing “ZRA-”, “ZRB-”, “ZRC-” is added respectively;

for fire-resistant cables, the writing “NH-” is added;

for low smoke and non-halogen cables, the writing “DWZR-” is added;

for low smoke and low-halogen cables, the writing “DDZR-” is added.

b. Refer to table 2 about the specification:

Table 2

| Rated voltage kV | Type | No. of Cores | Nominal Cross-sectional Area mm2 |
| --- | --- | --- | --- |
| 0.6/1 | VV VLV VY VLY VV22 VLV22 VV23 VLV23 VV32 VLV32 VV33 VLV33 VV42 VLV42 VV43 VLV43 | 1 | 1.5―800 |
|  |  | 2 | 1.5―400 |
|  |  | 3 | 1.5―400 |
|  |  | 4 | 4―400 |
|  |  | 3＋1 | 4―400 |
|  |  | 4＋1 | 6―300 |
|  |  | 3＋2 | 6―300 |
|  |  | 5 | 1.5―300 |

Note:

Armor of single core cable used for A.C system should be non-magnetic material except for special construction.

- Referential data:

outer diameter, weight (see table 3-table 12) and construction (see fig.1-fig. 13)

Nominal thickness of  insulation:

| Nominal Cross-sectional Area of Conductormm2 | 1.5、2.5 | 4～6 | 25、35 | 50、70 | 90、120 | 150 | 185 | 240 | 300 | 400 | 500～800 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Nominal Thickness of Insulation mm | 0.7 | 1.0 | 1.2 | 1.4 | 1.6 | 1.8 | 2.0 | 2.2 | 2.4 | 2.6 | 2.8 |

Single core non-armored cable                                                 Table3

| No. of Core × Cross-sectional Area mm2 | Non-armored Cable |  |  |
| --- | --- | --- | --- |
|  | Approx. Outer Diameter mm | Approx. Weight kg/km |  |
|  |  | VV | VLV |
| 1×1.5 | 6.1 | 50 | 41 |
| 1×2.5 | 6.5 | 63 | 47 |
| 1×4 | 7.4 | 87 | 62 |
| 1×6 | 7.9 | 110 | 73 |
| 1×10 | 9.2 | 162 | 99 |
| 1×16 | 10.2 | 226 | 126 |
| 1×25 | 12.0 | 331 | 175 |
| 1×35 | 13.1 | 431 | 214 |
| 1×50 | 14.9 | 577 | 279 |
| 1×70 | 16.7 | 779 | 356 |
| 1×95 | 19.1 | 1064 | 476 |
| 1×120 | 20.6 | 1293 | 560 |
| 1×150 | 23.0 | 1613 | 695 |
| 1×185 | 25.4 | 2001 | 856 |
| 1×240 | 28.7 | 2614 | 1100 |
| 1×300 | 31.7 | 3233 | 1346 |

Two Cores Cable                                                                Table 4

| No. of Core × Cross-sectional Area mm2 | Non-armored Cable |  |  | Steel-tape Armored Cable |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Approx. Outer Diameter mm | Approx. Weight kg/km |  | Approx. Outer Diameter mm | Approx. Weight kg/km |  |
|  |  | VV | VLV |  | VV | VLV |
| 2×1.5 | 9.8×6.7 | 94 | 75 | － | － | － |
| 2×2.5 | 10.6×7.1 | 119 | 89 | － | － | － |
| 2×4 | 14.0 | 213 | 163 | 16.8 | 383 | 334 |
| 2×6 | 15.1 | 263 | 188 | 17.9 | 446 | 370 |
| 2×10 | 17.7 | 372 | 244 | 20.5 | 586 | 458 |
| 2×16 | 19.8 | 513 | 310 | 22.6 | 752 | 550 |
| 2×25 | 22.1 | 736 | 426 | 25.5 | 987 | 677 |
| 2×35 | 24.1 | 949 | 515 | 27.5 | 1267 | 833 |
| 2×50 | 24.1 | 1276 | 656 | 27.5 | 1824 | 1204 |
| 2×70 | 25.3 | 1712 | 844 | 29.7 | 2324 | 1456 |
| 2×95 | 28.1 | 2168 | 990 | 33.2 | 2876 | 1698 |
| 2×120 | 31.9 | 2570 | 1082 | 37.3 | 3344 | 1856 |
| 2×150 | 34.7 | 3220 | 1360 | 39.8 | 4114 | 2254 |
| 2×185 | 42.1 | 3969 | 1675 | 47.6 | 4964 | 2670 |

Note:  The conductor of black writing is round and the conductor of red writing is sector shape.

Three Cores Cable                                                          Table 5

| No. of Core × Cross-sectional Area mm2 | Non-armored Cable |  |  | Steel-tape Armored Cable |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Approx. Outer Diameter mm | Approx. Weight kg/km |  | Approx. Outer Diameter mm | Approx. Weight kg/km |  |
|  |  | VV | VLV |  | VV | VLV |
| 3×1.5 | 11.9 | 148 | 120 | － | － | － |
| 3×2.5 | 12.8 | 187 | 140 | － | － | － |
| 3×4 | 14.7 | 265 | 191 | 17.5 | 443 | 369 |
| 3×6 | 15.8 | 336 | 224 | 18.6 | 527 | 415 |
| 3×10 | 18.6 | 501 | 309 | 21.4 | 726 | 534 |
| 3×16 | 20.9 | 677 | 319 | 23.7 | 946 | 643 |
| 3×25 | 24.0 | 1017 | 547 | 27.4 | 1315 | 845 |
| 3×35 | 22.2 | 1315 | 617 | 25.4 | 1669 | 972 |
| 3×50 | 25.9 | 1800 | 818 | 30.3 | 2448 | 1467 |
| 3×70 | 28.7 | 2447 | 1066 | 33.1 | 3156 | 1780 |
| 3×95 | 33.1 | 3230 | 1403 | 37.3 | 4029 | 2202 |
| 3×120 | 35.8 | 3890 | 1654 | 40.0 | 4751 | 2515 |
| 3×150 | 39.8 | 4550 | 2051 | 44.6 | 5871 | 3067 |
| 3×185 | 44.0 | 5908 | 2498 | 48.6 | 7005 | 3596 |
| 3×240 | 48.9 | 7740 | 3214 | 54.0 | 9004 | 4478 |

Note:  The conductor of black writing is round and the conductor of red writing is sector shape.

Three Cores Cable                                                           Table 6

| No. of Core × Cross-sectional Area mm2 | Thin Steel-wire Armored Cable |  |  |
| --- | --- | --- | --- |
|  | Approx. Outer Diameter mm | Approx. Weight kg/km |  |
|  |  | VV32 | VLV32 |
| 3×35 | 27.6 | 2131 | 1433 |
| 3×50 | 32.3 | 2961 | 1979 |
| 3×70 | 35.1 | 3721 | 2344 |
| 3×95 | 39.5 | 4686 | 2859 |
| 3×120 | 43.1 | 5834 | 3598 |
| 3×150 | 47.8 | 7075 | 4271 |
| 3×185 | 51.8 | 8336 | 4926 |
| 3×240 | 57.1 | 10482 | 5956 |

3＋1Core Cable                                                             Table 7

| No. of Core × Cross-sectional Area mm2 | Non-armored Cable |  |  | Steel-tape Armored Cable |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Approx. Outer Diameter mm | Approx. Weight kg/km |  | Approx. Outer Diameter mm | Approx. Weight kg/km |  |
|  |  | VV | VLV |  | VV22 | VLV22 |
| 3×4＋1×2.5 | 15.3 | 313 | 223 | 18.2 | 499 | 409 |
| 3×6＋1×4 | 16.8 | 405 | 268 | 19.6 | 609 | 472 |
| 3×10＋1×6 | 19.5 | 594 | 365 | 22.3 | 831 | 610 |
| 3×16＋1×10 | 22.2 | 834 | 468 | 25.0 | 1103 | 736 |
| 3×25＋1×16 | 26.0 | 1219 | 649 | 28.8 | 1534 | 964 |
| 3×35＋1×16 | 24.4 | 1625 | 727 | 27.6 | 1914 | 1116 |
| 3×50＋1×25 | 28.2 | 2122 | 980 | 32.4 | 2809 | 1668 |
| 3×70＋1×35 | 31.4 | 2869 | 1276 | 35.6 | 3631 | 2008 |
| 3×95＋1×50 | 36.4 | 3801 | 1675 | 40.6 | 4676 | 2550 |
| 3×120＋1×70 | 38.9 | 4656 | 1999 | 43.9 | 5630 | 2974 |
| 3×150＋1×70 | 43.0 | 5632 | 2408 | 47.6 | 6674 | 3450 |
| 3×185＋1×95 | 47.4 | 6960 | 2961 | 52.0 | 8140 | 4140 |
| 3×240＋1×120 | 52.6 | 9018 | 3758 | 57.7 | 10376 | 5115 |

Note:  The conductor of black writing is round and the conductor of red writing is sector shape.

3＋1 Core Cable                                                                Table 8

| No. of Core × Cross-sectional Area mm2 | Thin Steel-wire Armored Cable |  |  |
| --- | --- | --- | --- |
|  | Approx. Outer Diameter mm | Approx. Weight kg/km |  |
|  |  | VV32 | VLV32 |
| 3×35＋1×16 | 29.8 | 2415 | 1618 |
| 3×50＋1×25 | 34.6 | 3398 | 2256 |
| 3×70＋1×35 | 37.8 | 4264 | 2671 |
| 3×95＋1×50 | 42.8 | 5403 | 3276 |
| 3×120＋1×70 | 46.7 | 6931 | 4275 |
| 3×150＋1×70 | 50.8 | 7980 | 4756 |
| 3×185＋1×95 | 55.2 | 9569 | 5570 |
| 3×240＋1×120 | 60.9 | 11947 | 6686 |

4 Cores Cable                                                                  Table 9

| No. of Core × Cross-sectional Area mm2 | Non-armored Cable |  |  | Steel-tape Armored Cable |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Approx. Outer Diameter mm | Approx. Weight kg/km |  | Approx. Outer Diameter mm | Approx. Weight kg/km |  |
|  |  | VV | VLV |  | VV22 | VLV22 |
| 4×4 | 15.9 | 328 | 229 | 18.7 | 521 | 422 |
| 4×6 | 17.1 | 421 | 271 | 19.9 | 629 | 479 |
| 4×10 | 20.2 | 537 | 381 | 23.0 | 882 | 628 |
| 4×16 | 22.8 | 890 | 486 | 25.6 | 1166 | 792 |
| 4×25 | 27.0 | 1314 | 890 | 29.8 | 1641 | 1014 |
| 4×35 | 24.1 | 1714 | 784 | 27.5 | 2110 | 1180 |
| 4×50 | 27.9 | 2361 | 1053 | 32.3 | 3055 | 1746 |
| 4×70 | 31.3 | 3226 | 1390 | 35.5 | 3982 | 2146 |
| 4×95 | 36.0 | 4252 | 1816 | 40.4 | 5135 | 2699 |
| 4×120 | 38.5 | 5119 | 2138 | 43.3 | 6103 | 3121 |
| 4×150 | 42.8 | 6409 | 2671 | 47.4 | 7483 | 3743 |
| 4×185 | 47.2 | 7796 | 3250 | 52.2 | 9015 | 4469 |
| 4×240 | 52.4 | 10217 | 4184 | 57.4 | 11566 | 5531 |

Note:  The conductor of black writing is round and the conductor of red writing is sector shape.

3+2 Cores Cable                                                            Table 10

| No. of Core × Cross-sectional Area mm2 | Non-armored Cable |  |  | Steel-tape Armored Cable |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Approx. Outer Diameter mm | Approx. Weight kg/km |  | Approx. Outer Diameter mm | Approx. Weight kg/km |  |
|  |  | VV | VLV |  | VV22 | VLV22 |
| 3×25＋2×16 | 27 | 1420 | 683 | 31 | 2212 | 1373 |
| 3×35＋2×16 | 29 | 1733 | 804 | 32 | 2601 | 1487 |
| 3×50＋2×25 | 33 | 2480 | 1129 | 38 | 3474 | 2100 |
| 3×70＋2×35 | 38 | 3381 | 1457 | 42 | 4455 | 2536 |
| 3×95＋2×50 | 43 | 4602 | 1956 | 48 | 5865 | 2986 |
| 3×120＋2×70 | 48 | 5770 | 2396 | 53 | 7190 | 3816 |
| 3×150＋2×70 | 52 | 6952 | 2881 | 57 | 8551 | 4479 |
| 3×185＋2×95 | 58 | 8780 | 3671 | 63 | 10696 | 5588 |
| 3×240＋2×120 | 64 | 10749 | 4445 | 69 | 13676 | 7373 |
| 3×300＋2×150 | 71 | 13849 | 5632 | 76 | 16272 | 8607 |

4+1 Core Cable                                                                Table 11

| No. of Core × Cross-sectional Area mm2 | Non-armored Cable |  |  | Steel-tape Armored Cable |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Approx. Outer Diameter mm | Approx. Weight kg/km |  | Approx. Outer Diameter mm | Approx. Weight kg/km |  |
|  |  | VV | VLV |  | VV22 | VLV22 |
| 4×25＋16 | 28 | 1535 | 730 | 32 | 2330 | 1525 |
| 4×35＋16 | 30 | 1948 | 877 | 35 | 2745 | 1674 |
| 4×50＋25 | 35 | 2723 | 1216 | 40 | 3700 | 2193 |
| 4×70＋35 | 40 | 3740 | 1580 | 44 | 4834 | 2675 |
| 4×95＋50 | 45 | 5096 | 2124 | 50 | 6059 | 3087 |
| 4×120＋70 | 51 | 6266 | 2571 | 55 | 7755 | 4060 |
| 4×150＋70 | 55 | 7813 | 3190 | 60 | 9480 | 4858 |
| 4×185＋95 | 61 | 9716 | 4004 | 66 | 12449 | 6737 |
| 4×240＋120 | 68 | 11943 | 4877 | 73 | 15006 | 7940 |
| 4×300＋150 | 75 | 15401 | 6171 | 81 | 18833 | 9603 |

5 Cores Cable                                                                     Table 12

| No. of Core × Cross-sectional Area mm2 | Non-armored Cable |  |  | Steel-tape Armored Cable |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Approx. Outer Diameter mm | Approx. Weight kg/km |  | Approx. Outer Diameter mm | Approx. Weight kg/km |  |
|  |  | VV | VLV |  | VV22 | VLV22 |
| 5×16 | 25 | 1020 | 520 | 29 | 1530 | 1030 |
| 5×25 | 28 | 1740 | 815 | 32 | 2618 | 1691 |
| 5×35 | 31 | 2287 | 1015 | 35 | 3281 | 2010 |
| 5×50 | 36 | 3120 | 1375 | 41 | 4310 | 2560 |
| 5×70 | 40 | 4301 | 1806 | 45 | 5648 | 3060 |
| 5×95 | 47 | 5880 | 2427 | 52 | 7551 | 4090 |
| 5×120 | 51 | 7105 | 2890 | 57 | 9183 | 4718 |
| 5×150 | 57 | 9115 | 3681 | 63 | 11428 | 5744 |
| 5×185 | 62 | 11197 | 4566 | 68 | 13706 | 6875 |
| 5×240 | 70 | 13805 | 5586 | 76 | 16625 | 8208 |
| 5×300 | 78 | 17850 | 7095 | 84 | 20986 | 10231 |

- Referential Carrying Capacity of Cable (see table 13-table 14):

a. Refer to table 13 about referential carrying capacity of single core PVC insulated power cable

Table 13

| Type | VV、VLV、VY、VLY |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Voltage | 0.6/1KV |  |  |  |  |  |  |  |  |  |
| Arrangement | ○ ○ ○ Trefoil (in contact) |  |  |  |  | ○○○ Parallel (the distance between two adjacent cables is the outer diameter of cable) |  |  |  |  |
| Installation Condition | In Air |  |  | Underground |  | In Air |  |  | Underground |  |
| Cross-sectional Area mm2 | Cu | Al |  | Cu | Al | Cu | Al |  | Cu | Al |
| 1.5 2.5 4 6 10 16 25 35 50 70 95 120 150 185 240 300 400 | 19 25 33 41 57 76 98 115 145 180 225 260 300 345 410 475 555 | － 19 26 34 44 59 76 90 110 140 175 200 230 270 320 370 440 |  | 27 36 47 58 78 100 130 155 185 255 270 310 350 395 455 515 585 | － 27 35 46 58 76 98 115 140 170 205 235 265 300 350 395 455 | 24 31 41 52 72 95 120 150 180 230 280 325 375 430 510 585 690 | － 24 32 42 55 73 96 115 140 175 215 250 290 335 395 455 540 |  | 29 38 49 61 83 105 135 160 195 240 285 325 365 415 480 545 625 | － 30 39 50 64 83 105 125 150 185 220 250 285 320 375 425 490 |
| Operating Temperature ℃ |  | 70 |  |  |  |  |  |  |  |  |
| Ambient Temperature ℃ |  | 40 | 25 |  |  | 40 |  | 25 |  |  |

(1)  ρw:  soil thermal resistivity without water loss   1.0 k..m/w.

(2)  The referential carrying capacity of 2 cores and above PVC insulated and sheathed power cable is stipulated in table 14.

(3)  Correction coefficient of current rating under different ambient temperature is stipulated in table 15.  (4)  Correction coefficient of current rating under different ground thermal resistivity is stipulated in table               16.

Table 14

| Cross-sectional Area mm2 | In Air |  |  |  |  | Underground |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Two Cores |  | Three Cores and above |  |  | Two Cores |  | Three Cores and above |  |
|  | VV | VLV | VV | VLV |  | VV | VLV | VV | VLV |
| 1.5 2.5 4 6 10 16 25 35 50 70 95 120 150 185 240 300 | 17 23 31 38 53 71 90 110 135 165 210 245 280 320 － － | － 18 24 32 42 55 70 86 105 130 165 190 215 250 － － | 15 19 26 32 46 60 77 95 115 145 185 210 245 280 335 375 | － 15 20 26 35 47 60 74 90 115 140 165 190 215 260 295 |  | 27 35 47 58 80 105 133 164 201 244 275 310 350 395 － － | － 28 36 45 62 82 104 127 159 186 210 245 275 310 － － | 22 30 39 49 68 89 107 131 159 195 231 262 300 337 390 435 | － 23 31 38 52 69 83 101 123 150 178 201 231 262 301 340 |
| Operating Temperature ℃ | 70 |  |  |  |  |  |  |  |  |
| Ambient Temperature ℃ | 40 |  |  |  | 25 |  |  |  |  |

Note: ρw: soil thermal resistivity without water loss.    1.0k..m/w.

Table 15

| Operating Temperature of Conductor℃ | Ambience | Different Ambient Temperature ℃ |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 |
| 70 | In Ground | 1.15 | 1.11 | 1.05 | 1.00 | 0.94 | 0.88 | － | － | － |
| 70 | In Air | 1.41 | 1.35 | 1.29 | 1.22 | 1.15 | 1.08 | 1.00 | 0.91 | 0.81 |

Table 16

| Voltage | Cross-sectional Area | Ground Thermal Resistivity |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| kV | mm2 | 0.8 | 1.0 | 1.2 | 1.5 | 2.0 |
| 1 | 35 and Up to 50－120 150－300 400 and above | 1.06 1.08 1.08 1.09 | 1.00 1.00 1.00 1.00 | 0.95 0.94 0.93 0.93 | 0.89 0.87 0.86 0.85 | 0.81 0.77 0.76 0.76 |

- Main Technical Data:

a. The finished cable should withstand the testing voltage (50Hz A.C.) at ambient temperature. The testing voltage is stipulated in Table 17. Single core non-armored cable must be tested after immersion in water for 1 hour.

Table 17

| Rated Voltage kV | Testing Voltage kV | Time min |
| --- | --- | --- |
| 0.6/1.0 | 3.5 | 5 |

Testing voltage shall be 2.4 times of the A.C. voltage when D.C. voltage is used in the test.

b. The cable should withstand D.C testing after installation. We suggest that the testing voltage should be 4U0 (U0 refer to voltage against ground of conductor). Time is 5 minutes.

c. Mechanical performance of the cable insulation and sheath is stipulated in table 18.

Special test of cable insulation and sheath is stipulated in table 19 and table20 respectively.

- Delivery Length:

The delivery length of the cable shall not be less than 100 meters.

With the amount of short strands being 10% of the total length, the length for each short strand is not less than 20 meters.

The delivery length can be decided through negotiation by both parties.

- Writing of type and size to order:

Please indicate the type, specification, voltage, standards and quantity.

For example, 1kV, 3 cores, 240mm2 aluminum conductor PVC insulated, PVC sheathed, steel-tape armored power cable, 4km.

Indicate as: VLV22-0.6/1.0 kV  3×240 mm2   4km  GB/T 12706-2002(or IEC60502)

Mechanical Performance of Insulation and Sheath            Table  18

| Item | Material |  |  |
| --- | --- | --- | --- |
|  | PVC Insulation | PVC Sheath | PE Sheath |
| Mechanical Performance before aging |  |  |  |
| Min. Tensile Strength N/mm2 | 12.5 | 12.5 | 10.0 |
| Min. Elongation at Break ％ | 150 | 150 | 300 |
| Mechanical Performance after aging in air-oven |  |  |  |
| Condition: Temperature (tolerance +℃) | 100 | 100 | 100 |
| Sustaining Time: days | 7 | 7 | 7 |
| Min. Tensile Strength N/mm2 | 12.5 | 12.5 | / |
| Max. Variation of Tensile Strength ％ | ±25 | ±25 | - |
| Min. Elongation at Break ％ | 150 | 150 | 300 |
| Max. Variation of Elongation at Break ％ | ±25 | ±25 | - |

Special Test of PVC Insulation and Sheath               Table 19

| Item | Material |  |
| --- | --- | --- |
|  | PVC Insulation | PVC Sheath |
| High Temperature Pressure Test |  |  |
| Testing Temperature (tolerance +℃) | 80 | 80 |
| Max. Indentation depth ％ | 50 | 50 |
| Low Temperature Characteristic Test |  |  |
| Low Temperature Winding Test before aging |  |  |
| Max. Diameter of Cable in Cold-bending Test mm | 12.5 | 12.5 |
| Testing Temperature (tolerance +2℃) | -15 | -15 |
| Low Temperature Elongation Test |  |  |
| Testing temperature (tolerance +2℃) | -15 | -15 |
| Low Temperature Impulse Test |  |  |
| Testing Temperature (tolerance +2℃) | - | 15 |
| Cracking Resistance (hot impulse) Test |  |  |
| Testing Temperature (tolerance +2℃) | 150 | 150 |
| Sustaining Time h | 1 | 1 |
| Water Absorption Test |  |  |
| Voltage Method |  |  |
| Testing Temperature (tolerance +2℃) | 70 | - |
| Sustaining Time days | 10 | - |

Special Test of PE Sheath                 Table 20

| Testing Item | PE Sheath |
| --- | --- |
| Melt Index |  |
| Max. Melt Index before Aging g/10Min | 0.4 |
| Min. Carbon Content ％ Min | 2.0 |