Rated Voltage up to 0.6/1kV XLPE Insulated Power Cable

- Standard:

GB/T12706-2002, IEC60502 or other relevant standards.

- Application Characteristics:

  - Max. permissive operating temperature of conductor in long-term is 90℃ and the max. short-circuit temperature (within 5s) is 250℃.

  - The ambient temperature during installation should be above 0℃ and the min. bending radius is as follows:

For single core cable: 20（D+d）±5％ mm

For multi-core cable: 15（D+d）±5％ mm

Where:

D is the actual outer diameter of cable,           mm;

d is the actual outer diameter of conductor,       mm.

3.  Type and Specification (refer to table 1):

Table 1

| Type | Name |
| --- | --- |
| YJV YJLV | XLPE insulated PVC sheathed power cable |
| YJY YJLY | XLPE insulated PE sheathed power cable |
| YJV22 YJLV22 | XLPE insulated PVC sheathed steel-tape armored power cable |
| YJV23 YJLV23 | XLPE insulated PE sheathed steel-tape armored power cable |
| YJV32 YJLV32 | XLPE insulated PVC sheathed thin steel-wire armored power cable |
| YJV33 YJLV33 | XLPE insulated PE sheathed thin steel-wire armored power cable |
| YJV42 YJLV42 | XLPE insulated PVC sheathed thick steel-wire armored power cable |
| YJV43 YJLV43 | XLPE insulated PE sheathed thick steel-wire armored power cable |

Note:

Our company can also produce flame-retardant, fire-resistant, anti-termite, low smoke and non-halogen cables respectively according to the requirements of customers.

eg.: for flame-retardant cables, the writing “ZRA-”, “ZRB-”, “ZRC-” is added respectively;

for fire-resistant cables, the writing “NH-” is added;

for low smoke and non-halogen cables, the writing “DWZR-” is added;

for low smoke and low-halogen cables, the writing “DDZR-” is added.

4.  Refer to table 2-table 10 about size of cable; Refer to fig.1-fig13 about the construction of cable:

Single Core Armored Cable                                                Table 2

| No. of Cores × Cross-sectional Area mm2 | Nominal Thickness of Insulation mm | Approx. Outer Diameter of Cable mm | Approx. Weight of Cable kg/km |  |
| --- | --- | --- | --- | --- |
|  |  |  | Copper | Aluminum |
| 1×4 | 0.7 | 6.6 | 70 | 45 |
| 1×6 | 0.7 | 7.1 | 91 | 54 |
| 1×10 | 0.7 | 8.4 | 137 | 75 |
| 1×16 | 0.7 | 9.4 | 198 | 99 |
| 1×25 | 0.9 | 10.8 | 292 | 138 |
| 1×35 | 0.9 | 11.8 | 390 | 173 |
| 1×50 | 1.0 | 13.3 | 538 | 229 |
| 1×70 | 1.1 | 15.2 | 727 | 300 |
| 1×95 | 1.1 | 16.9 | 961 | 385 |
| 1×120 | 1.2 | 18.5 | 1184 | 466 |
| 1×150 | 1.4 | 20.7 | 1504 | 589 |
| 1×185 | 1.6 | 22.7 | 1838 | 712 |
| 1×240 | 1.7 | 25.4 | 2353 | 899 |
| 1×300 | 1.8 | 28.0 | 2932 | 1107 |
| 1×400 | 2.0 | 32.1 | 3883 | 1471 |
| 1×500 | 2.2 | 35.8 | 4900 | 1838 |
| 1×630 | 2.4 | 39.9 | 6157 | 2297 |
| 1×800 | 2.6 | 44.6 | 7795 | 2877 |

Note: The red writing means the conductor is compacted circular.

Single Core Armored Cable                                               Table 3

| No. of Cores ×Cross-sectional Area mm2 | Nominal Thickness of Insulation mm | Approx. Outer Diameter of Cable mm | Approx. Weight of Cable kg/km |  |
| --- | --- | --- | --- | --- |
|  |  |  | YJV62 | YJLV62 |
| 1×10 | 0.7 | 14.4 | 312 | 250 |
| 1×16 | 0.7 | 15.5 | 391 | 292 |
| 1×25 | 0.9 | 17.2 | 515 | 360 |
| 1×35 | 0.9 | 18.3 | 631 | 414 |
| 1×50 | 1.0 | 19.6 | 798 | 488 |
| 1×70 | 1.1 | 21.2 | 1017 | 583 |
| 1×95 | 1.1 | 23.0 | 1285 | 696 |
| 1×120 | 1.2 | 24.9 | 1559 | 815 |
| 1×150 | 1.4 | 26.8 | 1881 | 951 |
| 1×185 | 1.6 | 29.3 | 2279 | 1132 |
| 1×240 | 1.7 | 32.1 | 2857 | 1369 |
| 1×300 | 1.8 | 34.8 | 3482 | 1622 |
| 1×400 | 2.0 | 36.5 | 4217 | 1804 |
| 1×500 | 2.2 | 40.2 | 5404 | 2342 |
| 1×630 | 2.4 | 44.3 | 6680 | 2819 |
| 1×800 | 2.6 | 49.2 | 8399 | 3480 |

Note: Armor of single core cable used for A.C voltage should be non-magnetic material except for special construction.

The red writing means that the conductor is compacted circular.

Two Cores Cable                                                            Table 4

| No. of Cores × Cross-sectional Area mm2 | Nominal Thickness of Insulation mm | Approx. Outer Diameter of Cable mm |  | Approx. Weight of Cable kg/km |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Non- armored | Steel-tape Armored | YJV | YJLV | YJV22 | YJLV22 |
| 2×1.5 | 0.7 | 10.2 | 13.4 | 102 |  | 217 | / |
| 2×2.5 | 0.7 | 11.0 | 14.2 | 127 | 96 | 252 | 221 |
| 2×4 | 0.7 | 11.8 | 15.0 | 169 | 120 | 302 | 253 |
| 2×6 | 0.7 | 12.8 | 16.0 | 213 | 144 | 358 | 291 |
| 2×10 | 0.7 | 15.6 | 18.8 | 323 | 201 | 499 | 376 |
| 2×16 | 0.7 | 17.6 | 20.8 | 463 | 267 | 662 | 465 |
| 2×25 | 0.9 | 20.2 | 23.4 | 671 | 362 | 899 | 590 |
| 2×35 | 0.9 | 22.4 | 25.6 | 875 | 449 | 1128 | 701 |
| 2×50 | 1.0 | 20.3 | 23.5 | 1055 | 466 | 1286 | 697 |
| 2×70 | 1.1 | 22.9 | 26.3 | 1459 | 616 | 1731 | 888 |
| 2×95 | 1.1 | 26.3 | 29.5 | 1968 | 812 | 2266 | 1110 |
| 2×120 | 1.2 | 28.7 | 32.5 | 2444 | 993 | 2875 | 1424 |
| 2×150 | 1.4 | 31.7 | 35.7 | 3053 | 1231 | 3513 | 1691 |
| 2×185 | 1.6 | 35.3 | 39.5 | 3758 | 1498 | 4301 | 2041 |
| 2×240 | 1.7 | 39.5 | 43.7 | 4824 | 1899 | 5431 | 2505 |
| 2×300 | 1.8 | 43.5 | 47.9 | 6028 | 2346 | 6716 | 3034 |
| 2×400 | 2.0 | 48.4 | 53.4 | 7851 | 3016 | 8686 | 3851 |

Note: The red writing means that the conductor is compacted sector.

Three Cores Cable                                              Table 5

| No. of Cores × Cross-sectional Area mm2 | Nominal Thickness of Insulation mm | Approx. Outer Diameter mm |  | Approx. Weight of Cable kg/km |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Non- Armored | Steel-tape Armored | YJV22 | YJLV22 | YJV | YJLV |
| 3×1.5 | 0.7 | 10.6 | 13.8 | 240 | / | 120 | / |
| 3×2.5 | 0.7 | 11.5 | 14.7 | 289 | 243 | 159 | 112 |
| 3×4 | 0.7 | 13.8 | 17.5 | 464 | 390 | 230 | 156 |
| 3×6 | 0.7 | 14.9 | 18.6 | 551 | 438 | 298 | 185 |
| 3×10 | 0.7 | 17.8 | 21.4 | 753 | 562 | 453 | 262 |
| 3×16 | 0.7 | 19.8 | 23.6 | 978 | 675 | 639 | 337 |
| 3×25 | 0.9 | 23.4 | 27.0 | 1344 | 874 | 945 | 475 |
| 3×35 | 0.9 | 25.8 | 29.5 | 1691 | 1037 | 1250 | 596 |
| 3×50 | 1.0 | 21.3 | 24.8 | 2129 | 1148 | 1701 | 720 |
| 3×70 | 1.1 | 24.7 | 28.2 | 3067 | 1690 | 2345 | 968 |
| 3×95 | 1.1 | 27.8 | 32.5 | 3863 | 2035 | 3062 | 1234 |
| 3×120 | 1.2 | 30.9 | 35.8 | 4621 | 2385 | 3722 | 1486 |
| 3×150 | 1.4 | 34.2 | 39.2 | 5659 | 2855 | 4674 | 1871 |
| 3×185 | 1.6 | 38.6 | 43.3 | 6796 | 3386 | 5669 | 2259 |
| 3×240 | 1.7 | 42.5 | 47.6 | 8692 | 4166 | 7428 | 2901 |
| 3×300 | 1.8 | 51.3 | 55.5 | 9801 | 4278 | 8952 | 3429 |
| 3×400 | 2.0 | 57.0 | 61.6 | 12672 | 5420 | 11678 | 4424 |

Note: The red writing means that the conductor is compacted sector.

Four Cores Cable                                                         Table 6

| No. of Cores × Cross-sectional Area mm2 | Nominal Thickness of Insulation mm | Approx. Outer Diameter mm |  | Approx. Weight of Cable kg/km |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Non- Armored | Steel-tape Armor | YJV22 | YJLV22 | YJV | YJLV |
| 4×1.5 | 0.7 | 11.4 | 13.7 | 274 | / | 146 | / |
| 4×2.5 | 0.7 | 12.4 | 14.4 | 332 | 270 | 193 | 131 |
| 4×4 | 0.7 | 18.1 | 14.6 | 534 | 436 | 284 | 185 |
| 4×6 | 0.7 | 19.5 | 15.9 | 644 | 494 | 372 | 222 |
| 4×10 | 0.7 | 22.5 | 18.9 | 900 | 644 | 645 | 390 |
| 4×16 | 0.7 | 25.1 | 21.5 | 1186 | 783 | 819 | 416 |
| 4×25 | 0.9 | 29.2 | 25.6 | 1656 | 1029 | 1220 | 593 |
| 4×35 | 0.9 | 30.5 | 28.5 | 2106 | 1234 | 1623 | 751 |
| 4×50 | 1.0 | 31.2 | 26.6 | 2882 | 1573 | 2203 | 895 |
| 4×70 | 1.1 | 35.1 | 30.3 | 3840 | 2004 | 3056 | 1221 |
| 4×95 | 1.1 | 39.2 | 33.9 | 4885 | 2449 | 3991 | 1554 |
| 4×120 | 1.2 | 41.9 | 37.3 | 5829 | 2848 | 4874 | 1893 |
| 4×150 | 1.4 | 46.6 | 41.5 | 7195 | 3457 | 6096 | 2358 |
| 4×185 | 1.6 | 51.3 | 45.8 | 8662 | 4116 | 7426 | 2880 |
| 4×240 | 1.7 | 56.2 | 50.6 | 11121 | 5086 | 9738 | 3703 |
| 4×300 | 1.8 | 59.3 | 63.7 | 12876 | 5511 | 11869 | 4504 |
| 4×400 | 2.0 | 66.0 | 71.0 | 16673 | 7002 | 15460 | 5789 |

Note: The red writing means that the conductor is compacted sector.

3+1 Core Cable                                                           Table7

| No. of Cores × Cross-sectional Area mm2 | Nominal Thickness of main Insulation mm | Approx. Outer Diameter of Cable mm |  | Approx. Weight of Cable kg/km |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Non- Armored | Steel-tape Armored | YJV22 | YJLV22 | YJV | YJLV |
| 3×2.5+1.5 | 0.7 | 11.4 | 16.5 | 318 |  | 181 | / |
| 3×4+2.5 | 0.7 | 14.4 | 18.0 | 522 | 432 | 275 | 185 |
| 3×6+4 | 0.7 | 15.6 | 19.0 | 625 | 488 | 358 | 221 |
| 3×10+6 | 0.7 | 18.3 | 22.0 | 847 | 618 | 535 | 306 |
| 3×16+10 | 0.7 | 20.9 | 25.0 | 1125 | 758 | 767 | 400 |
| 3×25+16 | 0.9 | 24.7 | 26.0 | 1552 | 981 | 1131 | 561 |
| 3×35+16 | 0.9 | 25.6 | 27.0 | 1890 | 1135 | 1432 | 677 |
| 3×50+25 | 1.0 | 27.8 | 31.0 | 2674 | 1532 | 1985 | 843 |
| 3×70+35 | 1.1 | 30.1 | 35.0 | 3501 | 1908 | 2719 | 1126 |
| 3×95+50 | 1.1 | 33.9 | 39.0 | 4448 | 2322 | 3589 | 1463 |
| 3×120+70 | 1.2 | 37.0 | 42.0 | 5410 | 2754 | 4440 | 1783 |
| 3×150+70 | 1.4 | 41.1 | 46.0 | 6485 | 3261 | 5388 | 2170 |
| 3×185+95 | 1.6 | 45.6 | 51.0 | 7882 | 3882 | 6648 | 2650 |
| 3×240+120 | 1.7 | 50.3 | 56.0 | 10022 | 4761 | 8642 | 3381 |
| 3×300+150 | 1.8 | 55.7 | 59.9 | 11325 | 4890 | 10405 | 3970 |
| 3×400+185 | 2.0 | 62.0 | 66.6 | 14537 | 6154 | 13455 | 5072 |

Note: The red writing means that the conductor is compacted sector.

Five Cores Cable                                                       Table 8

| No. of Cores × Cross-sectional Area mm2 | Nominal Thickness of Insulation mm | Approx. Outer Diameter of Cable mm |  | Approx. Weight of Cable kg/km |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Non- armored | Steel-tape Armored | YJV | YJLV | YJV22 | YJLV22 |
| 5×1.5 | 0.7 | 11.4 | 14.4 | 165 | / | 301 | / |
| 5×2.5 | 0.7 | 12.5 | 15.5 | 222 | 144 | 371 | 294 |
| 5×4 | 0.7 | 13.7 | 16.7 | 309 | 188 | 472 | 351 |
| 5×6 | 0.7 | 15.1 | 18.1 | 418 | 242 | 597 | 422 |
| 5×10 | 0.7 | 18.7 | 21.7 | 656 | 349 | 875 | 569 |
| 5×16 | 0.7 | 21.5 | 24.5 | 967 | 475 | 1217 | 726 |
| 5×25 | 0.9 | 24.9 | 27.9 | 1444 | 673 | 1734 | 963 |
| 5×35 | 0.9 | 27.9 | 31.1 | 1921 | 855 | 2258 | 1191 |
| 5×50 | 1.0 | 32.0 | 35.3 | 2597 | 1124 | 2982 | 1509 |
| 5×70 | 1.1 | 37.3 | 41.0 | 3649 | 1540 | 4218 | 2110 |
| 5×95 | 1.1 | 42.1 | 45.8 | 4896 | 2006 | 5537 | 2647 |
| 5×120 | 1.2 | 46.4 | 50.4 | 6095 | 2467 | 6845 | 3217 |
| 5×150 | 1.4 | 52.4 | 56.4 | 7666 | 3110 | 8510 | 3953 |
| 5×185 | 1.6 | 58.5 | 62.7 | 9507 | 3856 | 10474 | 4823 |
| 5×240 | 1.7 | 65.3 | 70.0 | 12197 | 4882 | 13336 | 6021 |
| 5×300 | 1.8 | 71.9 | 76.6 | 15234 | 6028 | 16485 | 7279 |

Note: The red writing means that the conductor is compacted circular.

4+1 Core Cable                                                           Table 9

| No. of Cores × Cross-sectional Area mm2 | Nominal Thickness of main Insulation mm | Approx. Outer Diameter of Cable mm |  | Approx. Weight of Cable kg/km |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Non- armored | Steel-tape Armored | YJV | YJLV | YJV22 | YJLV22 |
| 4×2.5+1.5 | 0.7 | 15.3 | 20.5 | 218 | / | 365 | / |
| 4×4+2.5 | 0.7 | 17.0 | 22.0 | 374 | 260 | 592 | 477 |
| 4×6+4 | 0.7 | 18.8 | 23.7 | 492 | 319 | 702 | 528 |
| 4×10+6 | 0.7 | 22.2 | 27.2 | 731 | 443 | 933 | 645 |
| 4×16+10 | 0.7 | 24.5 | 29.6 | 1034 | 577 | 1351 | 893 |
| 4×25+16 | 0.9 | 27.7 | 32.9 | 1501 | 778 | 1809 | 1087 |
| 4×35+16 | 0.9 | 30.2 | 36.0 | 1811 | 967 | 2289 | 1445 |
| 4×50+25 | 1.0 | 34.9 | 40.5 | 2687 | 1284 | 3287 | 1884 |
| 4×70+35 | 1.1 | 39.6 | 45.6 | 3639 | 1674 | 4201 | 2341 |
| 4×95+50 | 1.1 | 44.2 | 50.4 | 4852 | 2169 | 5861 | 3278 |
| 4×120+70 | 1.2 | 47.8 | 52.9 | 6076 | 2644 | 7368 | 4237 |
| 4×150+70 | 1.4 | 53.4 | 60.1 | 7424 | 3245 | 8580 | 5108 |
| 4×185+95 | 1.6 | 59.2 | 64.8 | 9114 | 3905 | 13019 | 7911 |
| 4×240+120 | 1.7 | 56.7 | 61.1 | 11586 | 5008 | 10621 | 4043 |
| 4×300+150 | 1.8 | 62.9 | 67.5 | 14381 | 6105 | 13284 | 5008 |

Note: The red writing means that the conductor is compacted tile shaped.

3+2 Cores Cable                                                          Table 10

| No. of Cores × Cross-sectional Area mm2 | Nominal Thickness of main Insulation mm | Approx. Outer Diameter of Cable mm |  | Approx. Weight of Cable kg/km |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Non- armored | Steel-tape Armored | YJV | YJLV | YJV22 | YJLV22 |
| 3×2.5+2×1.5 | 0.7 | 15.5 | 20.5 | 206 | / | 350 | / |
| 3×4+2×2.5 | 0.7 | 16.9 | 21.9 | 354 | 250 | 653 | 529 |
| 3×6+2×4 | 0.7 | 18.2 | 23.3 | 461 | 301 | 785 | 615 |
| 3×10+2×6 | 0.7 | 20.7 | 25.7 | 706 | 444 | 1030 | 770 |
| 3×16+2×10 | 0.7 | 23.8 | 28.8 | 1004 | 582 | 1390 | 983 |
| 3×25+2×16 | 0.9 | 27.2 | 32.2 | 1441 | 776 | 1932 | 1276 |
| 3×35+2×16 | 0.9 | 29.1 | 34.2 | 1719 | 866 | 2589 | 1802 |
| 3×50+2×25 | 1.0 | 32.8 | 37.8 | 2386 | 1139 | 3471 | 2423 |
| 3×70+2×35 | 1.1 | 37.5 | 43.0 | 3264 | 1518 | 4521 | 2974 |
| 3×95+2×50 | 1.1 | 41.6 | 46.1 | 4342 | 1940 | 5812 | 3509 |
| 3×120+2×70 | 1.2 | 47.0 | 53.3 | 5569 | 2450 | 7370 | 4310 |
| 3×150+2×70 | 1.4 | 50.6 | 56.8 | 6527 | 2846 | 8998 | 5418 |
| 3×185+2×95 | 1.6 | 52.2 | 57.0 | 8187 | 3485 | 11076 | 6473 |
| 3×240+2×120 | 1.7 | 53.7 | 57.9 | 9457 | 3617 | 10345 | 4506 |
| 3×300+2×150 | 1.8 | 59.5 | 63.9 | 11831 | 4485 | 12842 | 5496 |

Note: The red writing means that the conductor is compacted tile shaped.

5.  Carrying Capacity of Cable:

a. Refer to table11 about the continuous carrying capacity of single core XLPE insulated power cable.

Table 11

| Type | YJV、YJLV、YJY、YJLY、 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Voltage | 0.6/1kV |  |  |  |  |  |  |  |  |  |
| Arrangement | ○ ○○ Trefoil (in contact) |  |  |  |  | ○○○ Parallel (the distance between two adjacent cables is the outer diameter of cable) |  |  |  |  |
| Installation | In Air |  | Underground |  |  | In Air |  |  | Underground |  |
| Cross-sectional Area（mm2） | Cu. | Al. | Cu. |  | Al. | Cu. | Al. |  | Cu. | Al. |
| 1.5 | 26 | / | 33 |  | / | 32 | / |  | 45 | / |
| 2.5 | 34 | 26 | 43 |  | 32 | 42 | 33 |  | 59 | 46 |
| 4 | 44 | 35 | 56 |  | 42 | 56 | 44 |  | 77 | 61 |
| 6 | 56 | 45 | 70 |  | 54 | 70 | 57 |  | 97 | 79 |
| 10 | 77 | 59 | 74 |  | 69 | 97 | 75 |  | 130 | 100 |
| 16 | 100 | 78 | 120 |  | 90 | 125 | 99 |  | 170 | 135 |
| 25 | 130 | 100 | 155 |  | 115 | 165 | 125 |  | 220 | 170 |
| 35 | 160 | 125 | 185 |  | 135 | 200 | 155 |  | 265 | 205 |
| 50 | 195 | 150 | 220 |  | 165 | 245 | 190 |  | 320 | 245 |
| 70 | 245 | 190 | 270 |  | 200 | 305 | 240 |  | 395 | 305 |
| 95 | 300 | 230 | 320 |  | 240 | 375 | 290 |  | 475 | 370 |
| 120 | 350 | 270 | 365 |  | 275 | 435 | 340 |  | 545 | 420 |
| 150 | 400 | 310 | 410 |  | 310 | 500 | 390 |  | 610 | 475 |
| 185 | 465 | 360 | 465 |  | 355 | 580 | 450 |  | 695 | 540 |
| 240 | 500 | 430 | 540 |  | 410 | 685 | 535 |  | 810 | 630 |
| 300 | 635 | 495 | 610 |  | 465 | 795 | 615 |  | 910 | 710 |
| Operating Temperature（℃） | 90 |  |  |  |  |  |  |  |  |  |
| Ambient Temperature（℃） | 40 |  |  | 25 |  | 40 |  | 25 |  |  |

b. Refer to table 12 about the continuous carrying capacity of multi-core XLPE insulated power cable.

| Type | YJV、YJLV、YJY、YJLY、YJV22、YJV22、YJV23、YJLV23、YJV32、YJLV32、YJV33、YJLV33 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Voltage | 0.6/1kV |  |  |  |  |  |  |  |
| Arrangement | Two Cores |  |  |  | Three cores and above |  |  |  |
| Installation | In Air |  | Underground |  | In Air |  | Underground |  |
| Cross-sectional Area（mm2） | Cu. | Al. | Cu. | Al. | Cu. | Al. | Cu. | Al. |
| 4 6 10 16 25 35 50 70 95 120 150 185 240 300 | 45 57 75 99 129 154 182 221 263 297 339 388 - - | 35 45 60 80 115 140 160 210 250 265 315 365 - - | 55 68 89 112 143 168 196 236 273 305 344 387 - - | 47 55 70 87 120 145 167 218 267 270 320 370 - - | 44 48 66 88 116 139 169 208 253 293 334 383 451 - | 33 40 55 68 89 100 137 169 210 265 290 350 410 - | 47 58 70 94 120 153 180 219 261 320 365 410 465 530 | 35 42 54 69 90 115 135 165 200 240 275 310 350 400 |
| Operating Temperature(℃） | 90 |  |  |  |  |  |  |  |
| Ambient Temperature(℃） | 40 |  | 25 |  | 40 |  | 25 |  |

c.  Refer to table 13 about the correction coefficient of carrying capacity under different ambient temperature.

Table 13

| Operating Temperature of Conductor （℃） | Ambient Temperature（℃） |  |  |  |  |  |  |  |  | Ground Temperature（℃） |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 5 | 10 | 15 | 20 | 25 | 30 | 35 |
| 90 | 1.22 | 1.18 | 1.13 | 1.09 | 1.04 | 1.00 | 0.95 | 0.90 | 0.84 | 1.14 | 1.11 | 1.07 | 1.04 | 1.00 | 0.96 | 0.92 |

d. Refer to table 14 about the correction coefficient of carrying capacity under different ground thermal resistivity.

Table 14

| Voltage | Cross-sectional Area | Ground Thermal Resistivity （℃-M/W） |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| kV | mm2 | 0.8 | 1.0 | 1.2 | 1.5 | 1.8 | 2.0 | 2.5 | 3.0 |
| 1 | Up to 35 50-120 150-300 | 1.06 1.08 1.08 | 1.00 1.00 1.00 | 0.95 0.94 0.93 | 0.89 0.87 0.86 | 0.84 0.80 0.79 | 0.81 0.77 0.76 | 0.75 0.70 0.69 | 0.71 0.65 0.64 |

6.  Main Technical Data of XLPE Insulated Cable:

a.  The D.C resistance (Ω/km)of conductor at 20℃ should not exceed the value stipulated in table 15.

Table 15

| Nominal Cross-sectional Area mm2 | 1.5 | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Cu. Core | 12.1 | 7.41 | 4.61 | 3.08 | 1.83 | 1.15 | 0.727 | 0.524 | 0.387 | 0.268 | 0.193 |
| Al. Core | / | 12.1 | 7.41 | 4.61 | 3.08 | 1.91 | 1.20 | 0.868 | 0.641 | 0.443 | 0.320 |

| Nominal Cross-sectional area mm2 | 120 | 150 | 185 | 240 | 400 | 500 | 630 | 800 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Cu. Core | 0.153 | 0.124 | 0.0991 | 0.0754 | 0.0470 | 0.0366 | 0.0283 | 0.0211 |
| Al. Core | 0.253 | 0.206 | 0.164 | 0.125 | 0.0778 | 0.0605 | 0.0469 | 0.0367 |

b.  Refer to table 16 about the voltage test.

| Rated Voltage kV Item |  | 0.6/1 |
| --- | --- | --- |
| A.C Voltage Test | Testing Voltage kV | 3.5 |
|  | Testing Time min | 5 |

c.  Refer to table 17 about the technical performance of low smoke low halogen flame-retardant PVC sheath.

Table 17

| No. | Testing Item | Low Smoke Low Halogen Sheath |
| --- | --- | --- |
|  | Max. Rated Temperature of Conductor ℃ | 90 |
| 1 1.1 1.2 | Mechanical Performance before Aging Min. Tensile Strength MPa Min. Elongation at Break ％ | 12.5 150 |
| 2 2.1 2.2 | Mechanical Performance after Aging in Air-oven Temperature ℃ Sustaining Time days Min. Tensile Strength Mpa Max. Variation of Tensile Strength % Min. Elongation at Break % Max. Variation of Elongation at Break % | 100±2 7 12.5 ±25 150 ±25 |
| 3 | Mass Loss Test Testing Temperature（tolerance ±2） ℃ Sustaining Time days Max. mass loss mg/cm2 | 100 7 2.0 |
| 4 | Pressure Test at high Temperature Testing Temperature（tolerance ±2） ℃ Loading Time h Max. Penetration Depth % | 80 4 50 |
| 5 | Cracking Resistance (hot impulse) Test Temperature ℃ Sustaining Time h | 150±3 1 |
| 6 | Elongation Test at low Temperature Temperature ℃ Min. Elongation % | -15±2 20 |
| 7 | Oxygen Index (no less than) | 30 |
| 8 | Max. Smoke Density (non flame mode) | 300 |
| 9 | Halogenidric Acid Emission mg/g | 100 |
| 10 | Dielectric Strength MV/m | 18 |
| 11 | Volume Resistivity at 20℃ Ω.m | 1×109 |
| 12 | Volume Resistivity at 70℃ Ω.m | - |

d.  Refer to table 18 about the technical requirements of low smoke non-halogen flame-ratardant polyolefin sheath.

Table 18

| No. | Testing Item | low smoke non-halogen polyolefin sheath |
| --- | --- | --- |
|  | Max. Rated Temperature of Conductor ℃ | 90 |
| 1 | Mechanical Performance before Aging Min. Tensile Strength Pa Min. Elongation at Break ％ | 10.0 125 |
| 2 | Mechanical Performance after Aging in Air-oven Condition: Temperature ℃ Temperature Tolerance (+2) ℃ Sustaining Time days Min. Tensile Strength Mpa Max. Variation of Tensile Strength % Min. Elongation at Break % Max. Variation of Elongation at Break % | 100±2 7 10.0 ±25 100 ±25 |
| 3 | Pressure Test under High Temperature Testing temperature（tolerance±2） ℃ Max. Indentation Depth % | 90 50 |