66～220kV XLPE Insulated Cable

Type & Name of Cables:

YJLW02（YJLLW02）: Cu. (Al.) conductor, XLPE insulated, corrugated aluminum sheath and PVC outer-sheath power cable.

YJLW03（YJLLW03）: Cu. (Al.) conductor, XLPE insulation, corrugated aluminum sheath and PE outer-sheath power cable.

YJLW02-Z（YJLLW02-Z）: Cu. (Al.) conductor, XLPE insulation, corrugated aluminum sheath, PVC outer-sheath and longitudinal waterproof power cable.

YJLW03-Z（YJLLW03-Z）: Cu. (Al.) conductor, XLPE insulation, corrugated aluminum sheath, PE outer-sheath and longitudinal waterproof power cable.

Application Circumstances:

PVC outer-sheath cable is mainly used in cable line which is anti-fire and has insulation requirements. PE outer-sheath cable is mainly used in directly buried cable line which has high requirement about the o outer-sheath insulation. For low temperature ambience (lower than -20℃), chemical liquid circumstances or poison cable, we should adopt PE outer-sheath

Structure:

- Conductor (800mm2 and below: compacted and circular, 800mm2 and above: Milliken)

- Conductor Shield

- XLPE Insulation

- Insulation Shield

- Longitudinal Waterproof Cushion Layer

- Corrugated Aluminum Sheath

- Corrosion-resistant Layer

- PE (PVC) Sheath and semi-conductive Coating

Product and Technique:

- Rod

Copper rod with diameter of 8mm is made of #1 copper plate with oxygen contents less than 18ppm and conductivity more than 101％ IACS.

Aluminum rod is made of aluminum ingot for electric purpose. After rare-earth elements treating specially, rod with diameter of 9.5 mm will have better electric and physical performance.

Copper rod is manufactured on upward oxygen-free copper rod production line.

Aluminum rod is manufactured on continuous rolling and casting sets.

2.  Conductor

Conductor is stranded from copper or aluminum wires. Conductor including and below 630mm2 is compacted circular stranded by draw dies with good concentricity and high compaction coefficient. Conductor above 800mm2 is segmented so as to reduce skin effects and low AC resistance and improve cable transmission capacity.

Compacted and circular conductor, sector shape segments for segmental conductor are manufactured on Frame Stranding Machine imported from CEECO in Canada which is completely controlled by computer. Sector segmental block can be twisted into helical shape with certain lay in order to finish stranding freely.

Sector segmental blocks can be stranded into circular shape with steady structure on Drum Stranding Machine.

Among the wires of conductor, water-absorption swelling material can be applied for conductor longitudinal waterproof.

- Insulation and Screen

Insulation is a super clean cross-linking material. Inner and outer screens are made from super clean, super-smooth, semi-conductive XLPE compound. Insulation, inner and outer screens are adopted by simultaneous triple-extrusion on vertical VCV line.

VCV line imported from NOKIA, Finland is completely controlled by computers with 96 meters height of vertical tower.

Insulation and screen material are fed by self-gravity under the circumstance of extra clean class reaching 1000.

Crosshead for bonded triple extrusion ensures smoothness of interfaces between screens and insulation.

Conductor preheater can drive the moisture out of conductor and ensure the uniformity of curing.

EX-RAY8000 eccentricity gage can facilitate to adjust concentricity and thickness of insulation and screens.

Curing and cooling adopt full dry process.

In-line stress elimination can relieve stress remainder in the cable core for improving the electrical and physical performance of cables and avoiding damages to cable terminations and joints.

- Semi-conductive Waterproof Cushion Layer

Imported top-quality semi-conductive waterproof swelling tapes are wrapped on insulated core as longitudinal waterproof cushion layer.

Suitable wrapping method results in completely effective and excellent longitudinal waterproof along cable screen.

- Metallic Sheath

Corrugated aluminum sheath not only satisfies the short circuit capacity, but also has an excellent strength, low weight, bending easily and good waterproof performance.

6.outer-sheath

outer-sheath is extruded with PE or PVC compound, also anti-termite compound as per the customer’s requirements. Semi-conductive coating is applied as an electrode of outer-sheath for withstand voltage test.

Main Construction Parameters and Related Electric Properties of XLPE Insulated Power Cables:

Main Construction Parameters

| Rated Voltage kV | Nominal Cross- section mm2 | Dia. Of Conductor mm | Thickness of Inner Screen mm | Thickness of Insulationmm | Thickness of Outer Screen mm | Approx. Thickness of Water-proof Cushion Layer mm | Thickness of Al. Sheath mm | Thickness of Oversheath mm | Overall Diameter of Cable mm | Approx. Weight of Cable kg/km |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  | Cu |  | Al |  |
|  |  |  |  |  |  |  |  |  |  | PVC Sheath | PE Sheath | PVC Sheath | PE Sheath |
| 38/66 | 150 | 14.5 | 1.2 | 13.0 | 1.0 | 2.0 | 2.0 | 3.5 | 69.9 | 4960 | 4675 | 4032 | 3714 |
|  | 185 | 16.2 | 1.2 | 13.0 | 1.0 | 2.0 | 2.0 | 3.5 | 71.6 | 5411 | 5119 | 4267 | 3975 |
|  | 240 | 18.4 | 1.2 | 12.0 | 1.0 | 2.0 | 2.0 | 3.5 | 71.8 | 5868 | 5575 | 4383 | 4090 |
|  | 300 | 20.6 | 1.2 | 12.0 | 1.0 | 2.0 | 2.0 | 3.5 | 74.0 | 6577 | 6275 | 4721 | 4419 |
|  | 400 | 23.8 | 1.2 | 12.0 | 1.0 | 2.0 | 2.0 | 3.5 | 77.2 | 7722 | 7406 | 5247 | 4931 |
|  | 500 | 26.6 | 1.2 | 12.0 | 1.0 | 2.0 | 2.0 | 3.5 | 80.0 | 8834 | 8506 | 5741 | 5413 |
|  | 630 | 30.0 | 1.2 | 12.0 | 1.0 | 2.0 | 2.0 | 3.5 | 83.4 | 10262 | 9916 | 6364 | 6021 |
|  | 800 | 34.0 | 1.2 | 12.0 | 1.0 | 2.0 | 2.0 | 3.5 | 87.4 | 12092 | 11732 | 7143 | 6783 |
|  | 1000 | 38.2 | 1.2 | 12.0 | 1.0 | 2.0 | 2.0 | 3.5 | 91.6 | 14206 | 13828 | 8019 | 7641 |
|  | 800* | 35.0 | 1.4 | 12.0 | 1.0 | 2.0 | 2.0 | 3.5 | 88.8 | 12230 | 11864 | - | - |
|  | 1000* | 40.2 | 1.4 | 12.0 | 1.0 | 2.0 | 2.0 | 3.5 | 95.0 | 14461 | 14068 | - | - |
|  | 1200* | 44.0 | 1.4 | 12.0 | 1.0 | 2.0 | 2.0 | 3.5 | 98.8 | 16545 | 16136 | 9121 | 8712 |
|  | 1400* | 46.0 | 1.4 | 12.0 | 1.0 | 2.0 | 2.0 | 3.5 | 100.8 | 18484 | 18067 | 9822 | 9405 |
|  | 1600* | 48.2 | 1.4 | 12.0 | 1.0 | 2.0 | 2.0 | 3.5 | 104.0 | 20474 | 20043 | 10574 | 10143 |
|  | 1800* | 52.0 | 1.4 | 12.0 | 1.0 | 2.0 | 2.0 | 3.5 | 107.8 | - | - | 11422 | 10974 |
|  | 2000* | 53.8 | 1.4 | 12.0 | 1.0 | 2.0 | 2.0 | 3.5 | 109.6 | - | - | 12107 | 11652 |
| 48/66 | 150 | 14.5 | 1.2 | 14.0 | 1.0 | 2.0 | 2.0 | 4.0 | 72.9 | 5318 | 4981 | 4390 | 4053 |
|  | 185 | 16.2 | 1.2 | 14.0 | 1.0 | 2.0 | 2.0 | 4.0 | 74.6 | 5779 | 5433 | 4634 | 4288 |
|  | 240 | 18.4 | 1.2 | 13.5 | 1.0 | 2.0 | 2.0 | 4.0 | 75.8 | 6348 | 5996 | 4863 | 4511 |
|  | 300 | 20.6 | 1.2 | 13.5 | 1.0 | 2.0 | 2.0 | 4.0 | 78.0 | 7071 | 6708 | 5215 | 4852 |
|  | 400 | 23.8 | 1.2 | 13.0 | 1.0 | 2.0 | 2.0 | 4.0 | 80.2 | 8117 | 7744 | 5642 | 5264 |
|  | 500 | 26.6 | 1.2 | 13.0 | 1.0 | 2.0 | 2.0 | 4.0 | 83.0 | 9244 | 8856 | 6150 | 5763 |
|  | 630 | 30.0 | 1.2 | 13.0 | 1.0 | 2.0 | 2.0 | 4.0 | 86.4 | 10688 | 10284 | 6790 | 6386 |
|  | 800 | 34.0 | 1.2 | 13.0 | 1.0 | 2.0 | 2.0 | 4.0 | 90.8 | 12545 | 12119 | 7595 | 7170 |
|  | 1000 | 38.2 | 1.2 | 13.0 | 1.0 | 2.0 | 2.0 | 4.0 | 94.6 | 14672 | 14228 | 8485 | 8043 |
|  | 800* | 35.0 | 1.4 | 13.0 | 1.0 | 2.0 | 2.0 | 4.0 | 91.8 | 12682 | 12252 | - | - |
|  | 1000* | 40.2 | 1.4 | 13.0 | 1.0 | 2.0 | 2.0 | 4.0 | 98.0 | 14941 | 14480 | - | - |
|  | 1200* | 44.0 | 1.4 | 13.0 | 1.0 | 2.0 | 2.0 | 4.0 | 101.8 | 17044 | 16565 | 9620 | 9140 |
|  | 1400* | 46.0 | 1.4 | 13.0 | 1.0 | 2.0 | 2.0 | 4.0 | 103.8 | 18993 | 18504 | 10331 | 9842 |
|  | 1600* | 48.2 | 1.4 | 13.0 | 1.0 | 2.0 | 2.0 | 4.0 | 107.0 | 20996 | 20491 | 11096 | 10592 |
|  | 1800* | 52.0 | 1.4 | 13.0 | 1.0 | 2.0 | 2.0 | 4.0 | 110.8 | - | - | 11962 | 11439 |
|  | 2000* | 53.8 | 1.4 | 13.0 | 1.0 | 2.0 | 2.0 | 4.0 | 112.6 | - | - | 12657 | 12124 |

Note: The conductors noted with * are milliken conductors, the following are the same.

| Rated Voltage kV | Nominal Cross- section mm2 | Dia. Of Conductor mm | Thickness of Inner Screen mm | Thickness of Insulationmm | Thickness of Outer Screen mm | Approx. Thickness of Water-proof Cushion Layer mm | Thickness of Al. Sheath mm | Thickness of Oversheath mm | Overall Diameter of Cable mm | Approx. Weight of Cable kg/km |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  | Cu |  | Al |  |
|  |  |  |  |  |  |  |  |  |  | PVC Sheath | PE Sheath | PVC Sheath | PE Sheath |
| 64/110 | 240 | 18.4 | 1.2 | 19.0 | 1.0 | 2.0 | 2.0 | 4.0 | 87.3 | 7719.1 | 7237.6 | 6234.2 | 5752.7 |
|  | 300 | 20.6 | 1.2 | 18.5 | 1.0 | 2.0 | 2.0 | 4.0 | 88.5 | 8346.8 | 7858.3 | 6490.7 | 6002.2 |
|  | 400 | 23.8 | 1.2 | 17.5 | 1.0 | 2.0 | 2.0 | 4.0 | 89.7 | 9291.9 | 8796.5 | 6817.1 | 6321.7 |
|  | 500 | 26.6 | 1.2 | 17.0 | 1.0 | 2.0 | 2.0 | 4.0 | 91.5 | 10319.9 | 9814.1 | 7226.4 | 6720.6 |
|  | 630 | 30.0 | 1.2 | 16.5 | 1.0 | 2.0 | 2.0 | 4.5 | 94.9 | 11872.5 | 11284.7 | 7974.7 | 7386.9 |
|  | 800 | 34.0 | 1.2 | 16.0 | 1.0 | 2.0 | 2.0 | 4.5 | 97.9 | 13627.4 | 13020.0 | 8677.8 | 8070.4 |
|  | 1000 | 38.2 | 1.2 | 16.0 | 1.0 | 2.0 | 2.3 | 4.5 | 102.7 | 16087.6 | 15449.0 | 9900.6 | 9262.0 |
|  | 800* | 35.0 | 1.6 | 16.0 | 1.0 | 2.0 | 2.0 | 4.5 | 99.7 | 13851.4 | 13232.3 | 8901.8 | 8282.7 |
|  | 1000* | 40.2 | 1.8 | 16.0 | 1.0 | 2.0 | 2.3 | 4.5 | 105.9 | 16492.2 | 15832.8 | 10305.2 | 9645.8 |
|  | 1200* | 44.0 | 1.8 | 16.0 | 1.0 | 2.0 | 2.3 | 4.5 | 109.7 | 18653.0 | 17968.9 | 11228.6 | 10544.5 |
|  | 1400* | 46.0 | 1.8 | 16.0 | 1.0 | 2.0 | 2.3 | 4.5 | 111.7 | 20632.5 | 19935.4 | 11970.7 | 11273.6 |
|  | 1600* | 48.2 | 1.8 | 16.0 | 1.0 | 2.0 | 2.3 | 4.5 | 113.9 | 22632.1 | 21920.7 | 12732.9 | 12021.5 |
|  | 1800* | 52.0 | 1.8 | 16.0 | 1.0 | 2.0 | 2.3 | 4.5 | 117.7 | 24792.9 | 24056.8 | 13656.3 | 12920.2 |
|  | 2000* | 53.8 | 1.8 | 16.0 | 1.0 | 2.0 | 2.3 | 4.5 | 119.5 | 26752.3 | 26004.4 | 14378.3 | 13630.4 |
| 76/132 | 240 | 18.4 | 1.2 | 19.0 | 1.2 | 2.0 | 2.0 | 4.0 | 87.7 | 7735.3 | 7251.5 | 6250.4 | 5766.6 |
|  | 300 | 20.6 | 1.2 | 19.0 | 1.2 | 2.0 | 2.0 | 4.0 | 89.9 | 8493.8 | 7997.3 | 6637.7 | 6141.2 |
|  | 400 | 23.7 | 1.2 | 19.0 | 1.2 | 2.0 | 2.0 | 4.0 | 93 | 9700.0 | 9185.5 | 7225.2 | 6710.7 |
|  | 500 | 16.6 | 1.2 | 19.0 | 1.2 | 2.0 | 2.0 | 4.0 | 85.9 | 9862.6 | 9389.1 | 6769.1 | 6295.6 |
|  | 630 | 30.0 | 1.2 | 19.0 | 1.2 | 2.0 | 2.0 | 4.5 | 100.3 | 12608.8 | 11985.8 | 8711.0 | 8088.0 |
|  | 800 | 34.0 | 1.2 | 18.0 | 1.2 | 2.0 | 2.0 | 4.5 | 102.3 | 14234.4 | 13598.4 | 9284.8 | 8648.8 |
|  | 1000 | 38.2 | 1.2 | 18.0 | 1.2 | 2.0 | 2.3 | 4.5 | 107.1 | 16731.5 | 16064.3 | 10544.5 | 9877.3 |
|  | 800* | 35.0 | 1.6 | 18.0 | 1.2 | 2.0 | 2.0 | 4.5 | 104.1 | 14468.9 | 13821.2 | 9519.3 | 8871.6 |
|  | 1000* | 40.2 | 1.8 | 18.0 | 1.2 | 2.0 | 2.3 | 4.5 | 110.3 | 17154.8 | 16466.8 | 10967.8 | 10279.8 |
|  | 1200* | 44.0 | 1.8 | 18.0 | 1.2 | 2.0 | 2.3 | 4.5 | 114.1 | 19337.8 | 18625.1 | 11913.4 | 11200.7 |
|  | 1400* | 46.0 | 1.8 | 18.0 | 1.2 | 2.0 | 2.3 | 4.5 | 116.1 | 21329.0 | 20603.2 | 12667.2 | 11941.4 |
|  | 1600* | 48.2 | 1.8 | 18.0 | 1.2 | 2.0 | 2.3 | 4.5 | 118.3 | 23341.5 | 22601.4 | 13442.3 | 12702.2 |
|  | 1800* | 52.0 | 1.8 | 18.0 | 1.2 | 2.0 | 2.3 | 4.5 | 122.1 | 25524.5 | 24759.7 | 14387.9 | 13623.1 |
|  | 2000* | 53.8 | 1.8 | 18.0 | 1.2 | 2.0 | 2.3 | 4.5 | 123.9 | 27494.3 | 26717.9 | 15120.3 | 14343.9 |

Note: The conductors noted with * are milliken conductors, the following are the same.

| Rated Voltage kV | Nominal Cross- section mm2 | Dia. Of Conductor mm | Thickness of Inner Screen mm | Thickness of Insulationmm | Thickness of Outer Screen mm | Approx. Thickness of Water-proof Cushion Layer mm | Thickness of Al. Sheath mm | Thickness of Oversheath mm | Overall Diameter of Cable mm | Approx. Weight of Cable kg/km |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  | Cu |  | Al |  |
|  |  |  |  |  |  |  |  |  |  | PVC Sheath | PE Sheath | PVC Sheath | PE Sheath |
| 127/220 | 400 | 23.8 | 2.0 | 27.0 | 1.0 | 2.0 | 2.4 | 5.0 | 114.6 | 13344.6 | 12552.6 | 10869.8 | 10077.8 |
|  | 500 | 26.6 | 2.0 | 27.0 | 1.0 | 2.0 | 2.4 | 5.0 | 117.4 | 14616.4 | 13804.3 | 11522.9 | 10710.8 |
|  | 630 | 30.0 | 2.0 | 26.0 | 1.0 | 2.0 | 2.4 | 5.0 | 118.8 | 15881.7 | 15059.5 | 11983.9 | 11161.6 |
|  | 800 | 34.0 | 2.0 | 25.0 | 1.0 | 2.0 | 2.4 | 5.0 | 120.8 | 17567.2 | 16730.4 | 12617.6 | 11780.8 |
|  | 1000 | 38.2 | 2.0 | 24.0 | 1.0 | 2.0 | 2.6 | 5.0 | 123.4 | 19756.9 | 18901.4 | 13569.9 | 12714.4 |
|  | 800* | 35.0 | 2.0 | 25.0 | 1.0 | 2.0 | 2.4 | 5.0 | 121.8 | 17698.0 | 16854.1 | 12748.4 | 11904.5 |
|  | 1000* | 40.2 | 2.0 | 24.0 | 1.0 | 2.0 | 2.6 | 5.0 | 125.4 | 20016.6 | 19146.7 | 13829.6 | 12959.7 |
|  | 1200* | 44.0 | 2.0 | 24.0 | 1.0 | 2.0 | 2.6 | 5.0 | 129.2 | 22288.0 | 21390.6 | 14863.6 | 13966.2 |
|  | 1400* | 46.0 | 2.0 | 24.0 | 1.0 | 2.0 | 2.6 | 5.0 | 131.2 | 24325.7 | 23413.8 | 15663.9 | 14752.0 |
|  | 1600* | 48.2 | 2.0 | 24.0 | 1.0 | 2.0 | 2.6 | 5.0 | 133.4 | 26389.4 | 25461.6 | 16490.2 | 15562.4 |
|  | 1800* | 52.0 | 2.0 | 24.0 | 1.0 | 2.0 | 2.8 | 5.0 | 137.6 | 28917.7 | 27959.6 | 17781.1 | 16823.0 |
|  | 2000* | 53.8 | 2.0 | 24.0 | 1.0 | 2.0 | 2.8 | 5.0 | 139.4 | 30932.8 | 29961.6 | 18558.8 | 17587.6 |

Note: The conductors noted with * are milliken conductors, the following are the same.

Max. Conductor Resistance                                                 　Unit:Ω/km

| Nominal Cross-section mm2 | D.C. Resistance（20℃） |  | A.C. Resistance（90℃） |  |
| --- | --- | --- | --- | --- |
|  | Cu | Al | Cu | Al |
| 150 | 0.124 | 0.206 | 0.159 | 0.264 |
| 185 | 0.0991 | 0.164 | 0.127 | 0.211 |
| 240 | 0.0754 | 0.125 | 0.0970 | 0.161 |
| 300 | 0.0601 | 0.100 | 0.0777 | 0.129 |
| 400 | 0.0470 | 0.0778 | 0.0614 | 0.101 |
| 500 | 0.0366 | 0.0605 | 0.0485 | 0.0787 |
| 630 | 0.0283 | 0.0469 | 0.0384 | 0.0616 |
| 800 | 0.0221 | 0.0367 | 0.0311 | 0.0489 |
| 1000 | 0.0176 | 0.0291 | 0.0260 | 0.0397 |
| 800* | 0.0221 | - | 0.0288 | - |
| 1000* | 0.0176 | - | 0.0232 | - |
| 1200* | 0.0151 | 0.0247 | 0.0201 | 0.0322 |
| 1400* | 0.0129 | 0.0212 | 0.0175 | 0.0278 |
| 1600* | 0.0113 | 0.0186 | 0.0156 | 0.0246 |
| 1800* | - | 0.0165 | - | 0.0220 |
| 2000* | - | 0.0149 | - | 0.0201 |

Capacitance                                                                   Unit:μF/km

| Nominal Cross-section mm2 | 38/66kV | 48/66kV | 64/110kV | 76/132kV | 127/220kV |
| --- | --- | --- | --- | --- | --- |
| 150 | 0.128 | 0.123 | - | - | - |
| 185 | 0.137 | 0.132 | - | - | - |
| 240 | 0.156 | 0.146 | 0.120 | 0.119 | - |
| 300 | 0.168 | 0.157 | 0.130 | 0.128 | - |
| 400 | 0.186 | 0.177 | 0.147 | 0.139 | 0.111 |
| 500 | 0.201 | 0.191 | 0.160 | 0.149 | 0.119 |
| 630 | 0.220 | 0.209 | 0.177 | 0.161 | 0.131 |
| 800 | 0.242 | 0.229 | 0.197 | 0.182 | 0.144 |
| 1000 | 0.264 | 0.250 | 0.213 | 0.197 | 0.160 |
| 800* | 0.244 | 0.231 | 0.200 | 0.185 | 0.147 |
| 1000* | 0.272 | 0.257 | 0.219 | 0.203 | 0.165 |
| 1200* | 0.292 | 0.276 | 0.234 | 0.216 | 0.176 |
| 1400* | 0.303 | 0.286 | 0.242 | 0.224 | 0.181 |
| 1600* | 0.314 | 0.297 | 0.251 | 0.232 | 0.187 |
| 1800* | 0.334 | 0.315 | 0.266 | 0.245 | 0.198 |
| 2000* | 0.344 | 0.324 | 0.274 | 0.252 | 0.203 |

Charging Current                                                                  Unit: A/km

| Nominal Cross-section mm2 | 38/66kV | 48/66kV | 64/110kV | 76/132kV | 127/220kV |
| --- | --- | --- | --- | --- | --- |
| 150 | 1.53 | 1.85 | - | - | - |
| 185 | 1.64 | 1.98 | - | - | - |
| 240 | 1.86 | 2.19 | 2.39 | 2.85 | - |
| 300 | 2.01 | 2.36 | 2.60 | 3.05 | - |
| 400 | 2.22 | 2.67 | 2.95 | 3.32 | 4.45 |
| 500 | 2.41 | 2.88 | 3.22 | 3.57 | 4.74 |
| 630 | 2.63 | 3.14 | 3.56 | 3.86 | 5.21 |
| 800 | 2.89 | 3.45 | 3.96 | 4.36 | 5.76 |
| 1000 | 3.16 | 3.77 | 4.28 | 4.70 | 6.37 |
| 800* | 2.92 | 3.49 | 4.01 | 4.41 | 5.87 |
| 1000* | 3.25 | 3.88 | 4.40 | 4.80 | 6.59 |
| 1200* | 3.49 | 4.16 | 4.71 | 5.17 | 7.01 |
| 1400* | 3.61 | 4.31 | 4.87 | 5.34 | 7.23 |
| 1600* | 3.75 | 4.47 | 5.05 | 5.53 | 7.47 |
| 1800* | 3.99 | 4.75 | 5.36 | 5.88 | 7.89 |
| 2000* | 4.10 | 4.89 | 5.50 | 6.01 | 8.08 |

Inductance                                                                     Unit: mH/km

| Nominal Cross-section mm2 | In Flat Formation ○○○ | In Trefoil Formation ○ ○○ | Nominal Cross-section mm2 | In Flat Formation ○○○ | In Trefoil Formation ○ ○○ |
| --- | --- | --- | --- | --- | --- |
| 150 | 0.761 | 0.807 | 1000 | 0.566 | 0.612 |
| 185 | 0.739 | 0.785 | 800* | 0.583 | 0.629 |
| 240 | 0.713 | 0.759 | 1000* | 0.555 | 0.602 |
| 300 | 0.690 | 0.736 | 1200* | 0.537 | 0.584 |
| 400 | 0.661 | 0.707 | 1400* | 0.528 | 0.575 |
| 500 | 0.639 | 0.685 | 1600* | 0.519 | 0.565 |
| 630 | 0.614 | 0.661 | 1800* | 0.504 | 0.550 |
| 800 | 0.589 | 0.636 | 2000* | 0.497 | 0.543 |

Max. Allowable Short-circuit Current of Conductor                                     Unit: KA

| Nominal Cross-sectionmm2 | Cu | Al | Nominal Cross-sectionmm2 | Cu | Al |
| --- | --- | --- | --- | --- | --- |
| 150 | 21.5 | 14.2 | 1000 | 143.1 | 94.5 |
| 185 | 26.5 | 17.5 | 800* | 114.5 | - |
| 240 | 34.3 | 22.7 | 1000* | 143.1 | - |
| 300 | 42.9 | 28.4 | 1200* | 171.7 | 113.4 |
| 400 | 57.2 | 37.8 | 1400* | 200.3 | 132.3 |
| 500 | 71.5 | 47.2 | 1600* | 228.9 | 151.2 |
| 630 | 90.1 | 59.5 | 1800* | - | 170.1 |
| 800 | 114.5 | 75.6 | 2000* | - | 189.0 |

Max. Allowable Short-circuit Current of Al. Sheath                                      Unit: KA

| Nominal Cross-sectionmm2 | 38/66kV | 48/66kV | 64/110kV | 76/132kV | 127/220kV |
| --- | --- | --- | --- | --- | --- |
| 150 | 36.3 | 37.5 | - | - | - |
| 185 | 37.4 | 38.6 | - | - | - |
| 240 | 37.5 | 39.3 | 48.2 | 46.5 | - |
| 300 | 38.8 | 40.7 | 48.9 | 47.8 | - |
| 400 | 40.8 | 42.0 | 49.7 | 49.8 | 62.1 |
| 500 | 42.5 | 43.8 | 50.9 | 51.7 | 63.9 |
| 630 | 44.6 | 45.9 | 52.4 | 54.0 | 64.7 |
| 800 | 47.1 | 48.3 | 54.3 | 55.0 | 66.0 |
| 1000 | 49.7 | 50.9 | 57.7 | 57.8 | 67.3 |
| 800* | 48.0 | 49.2 | 55.7 | 55.9 | 66.6 |
| 1000* | 51.8 | 53.0 | 59.2 | 59.9 | 68.6 |
| 1200* | 54.1 | 55.4 | 61.5 | 62.3 | 70.9 |
| 1400* | 55.4 | 56.6 | 62.8 | 63.5 | 72.7 |
| 1600* | 57.3 | 58.6 | 64.7 | 65.5 | 74.1 |
| 1800* | 59.7 | 60.9 | 67.1 | 67.8 | 76.4 |
| 2000* | 60.8 | 62.0 | 68.2 | 68.9 | 77.6 |

Positive and Negative Sequence Impedance and Zero Sequence Impedance (In Flat Formation)  Unit: Ω/km

| Rated Voltage kV | Nominal Cross-section mm2 | Copper Conductor |  | Aluminum Conductor |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Positive and Negative Sequence Impedance | Zero Sequence Impedance | Positive and Negative Sequence Impedance | Zero Sequence Impedance |
| 38/66 | 150 | 0.159+j0.238 | 0.254+j0.131 | 0.264+j0.238 | 0.359+j0.131 |
|  | 185 | 0.127+j0.232 | 0.219+j0.125 | 0.211+j0.232 | 0.303+j0.125 |
|  | 240 | 0.0970+j0.224 | 0.189+j0.113 | 0.161+j0.224 | 0.253+j0.113 |
|  | 300 | 0.0777+j0. 216 | 0.166+j0.108 | 0.129+j0.216 | 0.218+j0.108 |
|  | 400 | 0.0613+j0.207 | 0.146+j0.107 | 0.101+j0.207 | 0.185+j0.107 |
|  | 500 | 0.0485+j0.200 | 0.129+j0.103 | 0.0787+j0.200 | 0.160+j0.103 |
|  | 630 | 0.0384+j0.193 | 0.116+j0.0980 | 0.0616+j0.193 | 0.139+j0.0980 |
|  | 800 | 0.0310+j0.185 | 0.104+j0.0936 | 0.0489+j0.185 | 0.122+j0.0936 |
|  | 1000 | 0.0259+j0.178 | 0.0952+j0.0897 | 0.0396+j0.178 | 0.109+j0.0897 |
|  | 800* | 0.0288+j0.183 | 0.102+j0.0929 | - | - |
|  | 1000* | 0.0232+j0.174 | 0.0897+j0.0887 | - | - |
|  | 1200* | 0.0201+j0.169 | 0.0937+j0.0859 | 0.0322+j0.169 | 0.958+j0.0859 |
|  | 1400* | 0.0174+j0.166 | 0.0796+j0.0845 | 0.0278+j0.166 | 0.900+j0.0845 |
|  | 1600* | 0.0155+j0.163 | 0.0756+j0.0835 | 0.0246+j0.163 | 0.846+j0.0835 |
|  | 1800* | - | - | 0.0220+j0.158 | 0.797+j0.0820 |
|  | 2000* | - | - | 0.0200+j0.156 | 0.767+j0.0815 |
| 48/66 | 150 | 0.159+j0.238 | 0.250+j0.133 | 0.256+j0.238 | 0.348+j0.133 |
|  | 185 | 0.127+j0.232 | 0.216+j0.128 | 0.204+j0.232 | 0.293+j0.128 |
|  | 240 | 0.0970+j0.224 | 0.185+j0.121 | 0.156+j0.224 | 0.243+j0.121 |
|  | 300 | 0.0777+j0.216 | 0.162+j0.116 | 0.125+j0.216 | 0.209+j0.116 |
|  | 400 | 0.0613+j0.207 | 0.143+j0.109 | 0.0974+j0.207 | 0.179+j0.109 |
|  | 500 | 0.0485+j0.200 | 0.127+j0.104 | 0.0762+j0.200 | 0.155+j0.104 |
|  | 630 | 0.0384+j0.193 | 0.114+j0.0998 | 0.0596+j0.193 | 0.135+j0.0998 |
|  | 800 | 0.0310+j0.185 | 0.102+j0.0954 | 0.0474+j0.185 | 0.119+j0.0954 |
|  | 1000 | 0.0259+j0.178 | 0.0935+j0.0912 | 0.0384+j0.178 | 0.106+j0.0912 |
|  | 800* | 0.0288+j0.183 | 0.0988+j0.0945 | - | - |
|  | 1000* | 0.0232+j0.174 | 0.0881+j0.0902 | - | - |
|  | 1200* | 0.0201+j0.169 | 0.0823+j0.0873 | 0.0312+j0.169 | 0.0934+j0.0873 |
|  | 1400* | 0.0174+j0.166 | 0.0783+j0.0859 | 0.269+j0.166 | 0.0878+j0.0859 |
|  | 1600* | 0.0155+j0.163 | 0.0743+j0.0848 | 0.0238+j0.163 | 0.0826+j0.0848 |
|  | 1800* | - | - | 0.0220+j0.151 | 0.0778+j0.0816 |
|  | 2000* | - | - | 0.0200+j0.142 | 0.0749+j0.0810 |

| Rated Voltage kV | Nominal Cross-section mm2 | Copper Conductor |  | Aluminum Conductor |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Positive and Negative Sequence Impedance | Zero Sequence Impedance | Positive and Negative Sequence Impedance | Zero Sequence Impedance |
| 64/110 | 240 | 0.0970+j0.211 | 0.168+j0.134 | 0.161+j0.211 | 0.232+j0.134 |
|  | 300 | 0.0777+j0.204 | 0.148+j0.128 | 0.129+j0.202 | 0.199+j0.128 |
|  | 400 | 0.0614+j0.195 | 0.131+j0.119 | 0.101+j0.195 | 0.170+j0.119 |
|  | 500 | 0.0425+j0.188 | 0.116+j0.114 | 0.0787+j0.188 | 0.146+j0.114 |
|  | 630 | 0.0384+j0.180 | 0.104+j0.108 | 0.0616+j0.180 | 0.123+j0.108 |
|  | 800 | 0.0311+j0.172 | 0.0946+j0.103 | 0.0489+j0.172 | 0.112+j0.103 |
|  | 1000 | 0.0260+j0.165 | 0.0857+j0.0988 | 0.0397+j0.165 | 0.0994+j0.0988 |
|  | 800* | 0.0288+j0.171 | 0.0906+j0.102 | - | - |
|  | 1000* | 0.0232+j0.162 | 0.0814+j0.0973 | - | - |
|  | 1200* | 0.0201+j0.156 | 0.0761+j0.0941 | 0.0322+j0.156 | 0.0882+j0.0941 |
|  | 1400* | 0.0175+j0.153 | 0.0724+j0.0925 | 0.0278+j0.153 | 0.0827+j0.0925 |
|  | 1600* | 0.0156+j0.150 | 0.0688+j0.0913 | 0.0246+j0.150 | 0.0788+j0.0913 |
|  | 1800* | - | - | 0.0220+j0.146 | 0.0734+j0.0888 |
|  | 2000* | - | - | 0.0200+j0.144 | 0.0706+j0.0877 |
| 76/132 | 240 | 0.0970+j0.224 | 0.171+j0.131 | 0.161+j0.224 | 0.235+j0.131 |
|  | 300 | 0.0777+j0.216 | 0.150+j0.126 | 0.129+j0.216 | 0.201+j0.126 |
|  | 400 | 0.0613+j0.208 | 0.131+j0.120 | 0.101+j0.208 | 0.170+j0.120 |
|  | 500 | 0.0485+j0.200 | 0.115+j0.115 | 0.0787+j0.200 | 0.145+j0.115 |
|  | 630 | 0.0384+j0.193 | 0.102+j0.110 | 0.0616+j0.193 | 0.126+j0.110 |
|  | 800 | 0.0310+j0.185 | 0.0937+j0.103 | 0.0489+j0.185 | 0.112+j0.103 |
|  | 1000 | 0.0259+j0.178 | 0.0855+j0.0933 | 0.0396+j0.178 | 0.0992+j0.0993 |
|  | 800* | 0.0288+j0.183 | 0.0904+j0.103 | - | - |
|  | 1000* | 0.0232+j0.174 | 0.0806+j0.0981 | - | - |
|  | 1200* | 0.0201+j0.169 | 0.0754+j0.0948 | 0.0322+j0.169 | 0.0875+j0.0948 |
|  | 1400* | 0.0174+j0.166 | 0.0717+j0.0933 | 0.0278+j0.166 | 0.0820+j0.0933 |
|  | 1600* | 0.0155+j0.163 | 0.0681+j0.0920 | 0.0246+j0.163 | 0.0772+j0.0920 |
|  | 1800* | - | - | 0.0220+j0.158 | 0.0728+j0.0895 |
|  | 2000* | - | - | 0.0200+j0.156 | 0.0700+j0.0884 |
| 127/220 | 400 | 0.0614+j0.195 | 0.117+j0.133 | 0.101+j0.195 | 0.156+j0.133 |
|  | 500 | 0.0485+j0.188 | 0.102+j0.128 | 0.0787+j0.188 | 0.133+j0.128 |
|  | 630 | 0.0384+j0.180 | 0.0916+j0.121 | 0.0616+j0.180 | 0.115+j0.121 |
|  | 800 | 0.0311+j0.172 | 0.0791+j0.116 | 0.0489+j0.172 | 0.101+j0.115 |
|  | 1000 | 0.0260+j0.165 | 0.0678+j0.107 | 0.0397+j0.165 | 0.0860+j0.109 |
|  | 800* | 0.0288+j0.171 | 0.0750+j0.114 | - | - |
|  | 1000* | 0.0232+j0.162 | 0.0678+j0.107 | - | - |
|  | 1200* | 0.0201+j0.156 | 0.0605+j0.104 | 0.0322+j0.156 | 0.0726+j0.104 |
|  | 1400* | 0.0175+j0.153 | 0.0568+j0.102 | 0.0278+j0.153 | 0.0672+j0.102 |
|  | 1600* | 0.0156+j0.150 | 0.0512+j0.101 | 0.0246+j0.150 | 0.0602+j0.100 |
|  | 1800* | - | - | 0.0220+j0.146 | 0.0565+j0.0977 |
|  | 2000* | - | - | 0.0201+j0.144 | 0.0494+j0.0968 |

Positive and Negative Sequence Impedance and Zero Sequence Impedance (In Trefoil Formation) Unit: Ω/km

| Rated Voltage kV | Nominal Cross-section mm2 | Copper Conductor |  | Aluminum Conductor |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Positive and Negative Sequence Impedance | Zero Sequence Impedance | Positive and Negative Sequence Impedance | Zero Sequence Impedance |
| 38/66 | 150 | 0.159+j0.237 | 0.254+j0.131 | 0.264+j0.237 | 0.359+j0.131 |
|  | 185 | 0.127+j0.230 | 0.219+j0.125 | 0.211+j0.230 | 0.303+j0.125 |
|  | 240 | 0.0970+j0.222 | 0.189+j0.113 | 0.161+j0.222 | 0.253+j0.113 |
|  | 300 | 0.0777+j0.215 | 0.166+j0.108 | 0.129+j0.215 | 0.218+j0.108 |
|  | 400 | 0.0613+j0.206 | 0.146+j0.107 | 0.101+j0.206 | 0.185+j0.107 |
|  | 500 | 0.0485+j0.199 | 0.129+j0.103 | 0.0787+j0.199 | 0.160+j0.103 |
|  | 630 | 0.0384+j0.191 | 0.116+j0.0980 | 0.0616+j0.191 | 0.139+j0.0980 |
|  | 800 | 0.0310+j0.183 | 0.104+j0.0936 | 0.0489+j0.183 | 0.122+j0.0936 |
|  | 1000 | 0.0259+j0.176 | 0.0952+j0.0897 | 0.0396+j0.176 | 0.109+j0.0897 |
|  | 800* | 0.0288+j0.182 | 0.102+j0.0929 | - | - |
|  | 1000* | 0.0232+j0.173 | 0.0897+j0.0887 | - | - |
|  | 1200* | 0.0201+j0.167 | 0.0937+j0.0859 | 0.0322+j0.167 | 0.958+j0.0859 |
|  | 1400* | 0.0174+j0.164 | 0.0796+j0.0845 | 0.0278+j0.164 | 0.900+j0.0845 |
|  | 1600* | 0.0155+j0.161 | 0.0756+j0.0835 | 0.0246+j0.161 | 0.846+j0.0835 |
|  | 1800* | - | - | 0.0220+j0.156 | 0.797+j0.0820 |
|  | 2000* | - | - | 0.0200+j0.155 | 0.767+j0.0815 |
| 48/66 | 150 | 0.159+j0.237 | 0.250+j0.133 | 0.256+j0.237 | 0.348+j0.133 |
|  | 185 | 0.127+j0.230 | 0.216+j0.128 | 0.204+j0.230 | 0.293+j0.128 |
|  | 240 | 0.0970+j0.222 | 0.185+j0.121 | 0.156+j0.222 | 0.243+j0.121 |
|  | 300 | 0.0777+j0.215 | 0.162+j0.116 | 0.125+j0.215 | 0.209+j0.116 |
|  | 400 | 0.0613+j0.206 | 0.143+j0.109 | 0.0974+j0.206 | 0.179+j0.109 |
|  | 500 | 0.0485+j0.199 | 0.127+j0.104 | 0.0762+j0.199 | 0.155+j0.104 |
|  | 630 | 0.0384+j0.191 | 0.114+j0.0998 | 0.0596+j0.191 | 0.135+j0.0998 |
|  | 800 | 0.0310+j0.183 | 0.102+j0.0954 | 0.0474+j0.183 | 0.119+j0.0954 |
|  | 1000 | 0.0259+j0.176 | 0.0935+j0.0912 | 0.0384+j0.176 | 0.106+j0.0912 |
|  | 800* | 0.0288+j0.182 | 0.0988+j0.0945 | - | - |
|  | 1000* | 0.0232+j0.173 | 0.0881+j0.0902 | - | - |
|  | 1200* | 0.0201+j0.167 | 0.0823+j0.0873 | 0.0312+j0.167 | 0.0934+j0.0873 |
|  | 1400* | 0.0174+j0.164 | 0.0783+j0.0859 | 0.0269+j0.164 | 0.0878+j0.0859 |
|  | 1600* | 0.0155+j0.162 | 0.0743+j0.0848 | 0.0238+j0.162 | 0.0826+j0.0848 |
|  | 1800* | - | - | 0.0220+j0.149 | 0.0778+j0.0816 |
|  | 2000* | - | - | 0.0200+j0.140 | 0.0749+j0.0810 |
| 64/110 | 240 | 0.0970+j0.209 | 0.168+j0.134 | 0.161+j0.209 | 0.232+j0.134 |
|  | 300 | 0.0777+j0.202 | 0.148+j0.128 | 0.129+j 0.202 | 0.199+j0.128 |
|  | 400 | 0.0614+j0.193 | 0.131+j0.119 | 0.101+j0.193 | 0.170+j0.119 |
|  | 500 | 0.0485+j0.186 | 0.116+j0.114 | 0.0787+j0.186 | 0.146+j0.114 |
|  | 630 | 0.0384+j0.179 | 0.104+j0.108 | 0.0616+j0.179 | 0.123+j0.108 |
|  | 800 | 0.0311+j0.171 | 0.0946+j0.103 | 0.0489+j0.171 | 0.112+j0.103 |
|  | 1000 | 0.0260+j0.164 | 0.0857+j0.0988 | 0.0397+j0.164 | 0.0994+j0.0988 |
|  | 800* | 0.0288+j0.169 | 0.0906+j0.102 | - | - |
|  | 1000* | 0.0232+j0.160 | 0.0814+j0.0973 | - | - |
|  | 1200* | 0.0201+j0.155 | 0.0761+j0.0941 | 0.0322+j0.155 | 0.0882q0.0941 |
|  | 1400* | 0.0175+j0.152 | 0.0724+ j0.0925 | 0.0278+j0.152 | 0.0827+j0.0925 |
|  | 1600* | 0.0156+j0.149 | 0.0688+j0.0913 | 0.0246+j0.149 | 0.0778+j0.0913 |
|  | 1800* | - | - | 0.0220+j0.144 | 0.0734+j0.0888 |
|  | 2000* | - | - | 0.0201+j0.142 | 0.0706+j0.0877 |

| Rated Voltage kV | Nominal Cross-section mm2 | Copper Conductor |  | Aluminum Conductor |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Positive and Negative Sequence Impedance | Zero Sequence Impedance | Positive and Negative Sequence Impedance | Zero Sequence Impedance |
| 76/132 | 240 | 0.0970+j0.222 | 0.171+j0.131 | 0.616+j0.222 | 0.235+j0.131 |
|  | 300 | 0.0777+j0.215 | 0.150+j0.126 | 0.129+j0.215 | 0.201+j0.126 |
|  | 400 | 0.0613+j0.206 | 0.131+j0.120 | 0.101+j0.206 | 0.170+j0.120 |
|  | 500 | 0.0485+j0.199 | 0.115+j0.115 | 0.0787+j0.199 | 0.145+j0.115 |
|  | 630 | 0.0384+j0.191 | 0.102+j0.110 | 0.0616+j0.191 | 0.126+j0.110 |
|  | 800 | 0.0310+j0.183 | 0.0937+j0.103 | 0.0489+j0.183 | 0.112+j0.103 |
|  | 1000 | 0.0259+j0.176 | 0.0855+j0.0933 | 0.0396+j0.176 | 0.0992+j0.0993 |
|  | 800* | 0.0288+j0.182 | 0.0904+j0.103 | - | - |
|  | 1000* | 0.0232+j0.173 | 0.0806+j 0.0981 | - | - |
|  | 1200* | 0.0201+j0.167 | 0.0754+j 0.0948 | 0.0322+j0.167 | 0.0875+j0.0948 |
|  | 1400* | 0.0174+j0.164 | 0.0717+j0.0933 | 0.0278+j0.164 | 0.0820+j0.0933 |
|  | 1600* | 0.0155+j0.162 | 0.0681+j0.0920 | 0.0246+j0.162 | 0.0772+j0.0920 |
|  | 1800* | - | - | 0.0220+j0.157 | 0.0728+j0.0895 |
|  | 2000* | - | - | 0.0200+j0.155 | 0.0700+j0.0884 |
| 127/220 | 400 | 0.0614+j0.193 | 0.117+j0.133 | 0.101+j0.193 | 0.156+j0.133 |
|  | 500 | 0.0485+j0.186 | 0.102+j 0.128 | 0.0787+j0.186 | 0.133+j0.128 |
|  | 630 | 0.0384+j0.179 | 0.0916+j0.121 | 0.0616+j0.179 | 0.115+j0.121 |
|  | 800 | 0.0311+j0.171 | 0.0791+j0.116 | 0.0489+j0.171 | 0.101+j0.115 |
|  | 1000 | 0.0260+j0.164 | 0.0678+j0.107 | 0.0397+j0.164 | 0.0860+j0.109 |
|  | 800* | 0.0288+j0.169 | 0.0750+j0.114 | - | - |
|  | 1000* | 0.0232+j0.160 | 0.0678+j0.107 | - | - |
|  | 1200* | 0.0201+j0.155 | 0.0605+j0.104 | 0.0322+j0.155 | 0.0726+j0.104 |
|  | 1400* | 0.0175+j0.152 | 0.0568+j0.102 | 0.0278+j0.152 | 0.0672+j0.102 |
|  | 1600* | 0.0156+j0.149 | 0.0512+j0.101 | 0.0246+j0.149 | 0.0602+j0.100 |
|  | 1800* | - | - | 0.0220+j0.144 | 0.0565+j0.0977 |
|  | 2000* | - | - | 0.0201+j0.142 | 0.0494+j0.0968 |

Continuous Current Rating (reference value)                                             Unit: A

| Rated Voltage kV | Nominal Cross-section mm2 | In Air |  |  |  | Directly Buried |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | In Flat Formation ○○○ |  | In Trefoil Formation ○ ○○ |  | In Flat Formation ○○○ |  | In Trefoil Formation ○ ○○ |  |
|  |  | Cu | Al | Cu | Al | Cu | Al | Cu | Al |
| 38/66 48/66 | 150 | 496 | 389 | 448 | 346 | 410 | 318 | 376 | 249 |
|  | 185 | 570 | 440 | 511 | 397 | 463 | 361 | 424 | 328 |
|  | 240 | 612 | 524 | 596 | 465 | 541 | 419 | 487 | 381 |
|  | 300 | 769 | 600 | 680 | 532 | 607 | 472 | 544 | 429 |
|  | 400 | 891 | 697 | 777 | 617 | 689 | 540 | 617 | 487 |
|  | 500 | 1031 | 811 | 887 | 7]0 | 780 | 617 | 694 | 554 |
|  | 630 | 1187 | 942 | 1010 | 815 | 887 | 703 | 71 l | 626 |
|  | 800 | 1357 | 1085 | 1142 | 935 | 987 | 790 | 853 | 706 |
|  | 1000 | 1520 | 1245 | 1257 | 996 | 1083 | 888 | 923 | 780 |
|  | 800* | 1411 | - | 1187 | - | 1026 | - | 887 | - |
|  | 1000* | 1610 | - | 133l | - | 1147 | - | 978 | - |
|  | 1200* | 1475 | 1407 | 1437 | 1 187 | 1229 | 988 | 1036 | 862 |
|  | 1400* | 1914 | 1542 | 1540 | 1280 | 1315 | 1060 | 1094 | 920 |
|  | 1600* | 2049 | 1656 | 1627 | 1369 | 1388 | 1127 | 1142 | 968 |
|  | 1800* | - | 1784 |  | 1448 | - | 1 188 | - | 1003 |
|  | 2000* | - | 1867 |  | 1517 | - | 1243 | - | 1050 |
| 64/110 | 240 | 650 | 505 | 590 | 460 | 504 | 393 | 480 | 369 |
|  | 300 | 745 | 580 | 672 | 527 | 571 | 446 | 542 | 417 |
|  | 400 | 870 | 680 | 769 | 608 | 652 | 513 | 619 | 475 |
|  | 500 | 100l | 790 | 878 | 701 | 744 | 586 | 700 | 542 |
|  | 630 | 1159 | 921 | 1001 | 811 | 844 | 672 | 787 | 619 |
|  | 800 | 1325 | 1062 | 1133 | 927 | 915 | 750 | 840 | 685 |
|  | 1000 | 1480 | 1211 | 1301 | 1040 | 988 | 837 | 906 | 757 |
|  | 800* | 1376 | - | 1178 | - | 950 | - | 873 | - |
|  | 1000* | 1567 | - | 1318 | - | 1046 | - | 960 | - |
|  | 1200* | 1715 | 1373 | 1423 | 1174 | 1123 | 930 | 1008 | 835 |
|  | 1400* | 1863 | 1495 | 1525 | 1267 | 1291 | 1045 | 1080 | 898 |
|  | 1600* | 1990 | 1609 | 1614 | 1352 | 1358 | 1180 | 1144 | 954 |
|  | 1800* | - | 1735 |  | 1433 | - | 1234 | - | 1008 |
|  | 2000* | - | 1816 |  | 1500 | - | 1305 | - | 1054 |

Continuous Current Rating (reference value)                                             Unit: A

| Rated Voltage kV | Nominal Cross-section mm2 | In Air |  |  |  | Directly Buried |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | In Flat Formation ○○○ |  | In Trefoil Formation ○ ○○ |  | In Flat Formation ○○○ |  | In Trefoil Formation ○ ○○ |  |
|  |  | Cu | Al | Cu | Al | Cu | Al | Cu | Al |
| 76/132 | 240 | 655 | 507 | 592 | 461 | 525 | 410 | 482 | 381 |
|  | 300 | 748 | 585 | 672 | 530 | 593 | 463 | 545 | 429 |
|  | 400 | 862 | 676 | 769 | 608 | 675 | 530 | 612 | 487 |
|  | 500 | 995 | 782 | 879 | 701 | 767 | 602 | 685 | 550 |
|  | 630 | 1145 | 908 | 997 | 807 | 862 | 689 | 766 | 621 |
|  | 800 | 1305 | 1048 | 1125 | 930 | 964 | 778 | 845 | 700 |
|  | 1000 | 1456 | 1190 | 1237 | 1038 | 1053 | 865 | 911 | 77l |
|  | 800* | 1356 | - | 1170 | - | 1002 | - | 877 | - |
|  | 1000* | 1542 | - | 1310 | - | 1115 | - | 965 | - |
|  | 1200* | 1685 | 1348 | 1415 | 1162 | 1190 | 930 | 1026 | 853 |
|  | 1400* | 1830 | 1470 | 1486 | 1260 | 1272 | 1031 | 1085 | 910 |
|  | 1600* | 1952 | 1585 | 1601 | 1348 | 1335 | 1095 | 1127 | 960 |
|  | 1800* | - | 1704 | - | 1425 | - | 1147 | - | 994 |
|  | 2000* | - | 1783 | - | 1491 | - | 1200 | - | 1040 |
| 127/220 | 400 | 849 | 663 | 76l | 600 | 708 | 554 | 607 | 482 |
|  | 500 | 976 | 777 | 866 | 693 | 809 | 636 | 679 | 549 |
|  | 630 | 1128 | 891 | 984 | 794 | 915 | 728 | 761 | 615 |
|  | 800 | 1285 | 1027 | 1110 | 910 | 1025 | 825 | 835 | 690 |
|  | 1000 | 1440 | 1170 | 1221 | 1020 | 1133 | 920 | 902 | 765 |
|  | 800* | 1335 | - | 1153 | - | 1067 | - | 867 | - |
|  | 1000* | 1525 | - | 1293 | - | 1200 | - | 955 | - |
|  | 1200* | 1677 | 133l | 1394 | 1145 | 1296 | 1030 | 1010 | 843 |
|  | 1400* | 1829 | 1453 | 1496 | 1238 | 1397 | 1118 | 1067 | 900 |
|  | 1600* | 1965 | 1572 | 1584 | 1322 | 1484 | 1195 | 1113 | 950 |
|  | 1800* | - | 1708 | - | 1405 | - | 1271 | - | 984 |
|  | 2000* | - | 1787 | - | 1470 | - | 1330 | - | 1030 |

Rating Factors of Current Rating under Different Ambient Temperature:

| Ambient Temp. |  | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rating Factor | In Air | 1.34 | 1.30 | 1.27 | 1.22 | 1.18 | 1.14 | 1.10 | 1.05 | 1.00 |
|  | Underground | 1.18 | 1.14 | 1.11 | 1.07 | 1.04 | 1.00 | 0.96 | 0.92 | 0.88 |

Rating Factors of Current Rating under Different Soil Thermal Resistivities:

| Soil thermal resistivity℃·m/w | 0.8 | 1.0 | 1.2 | 1.5 | 1.8 | 2．0 | 2.5 | 3.0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rating factor | 1.07 | 1.06 | 1.0 | 0.92 | 0.86 | 0.83 | 0.75 | 0.70 |

Property parameters which are referred are based on the following conditions.

- Three-phase system laid in single circuit with a space of 250mm between the conditions and conductor temperature is 90℃.

- Type of earth bonding of metallic sheath: In single point bonding or cross-bonding.

- In air, ambient temperature 40℃, sheltered from direct solar radiations.

Directly buried, with 1m depth in a soil of 25℃, thermal resistivity 1.2℃·m/w.

- Short circuit currents calculated according to IEC 949 based on thermal insulation, Initial temperature:

for conductor 90℃, for metallic sheath 80℃，final temperature: 250℃, duration: 1 second.