6~35kV XLPE Insulated Power Cable

For XLPE insulated power cable, either chemical method or physical method to transform the molecular structure of PE from straight-chain into network i.e. thermoplastic PE had been transformed into thermosetting XLPE. After cross linking, the mechanical strength of the cable and the ambient stress resistance have been greatly improved, while its excellent electrical and heat aging properties are still maintained.

XLPE insulated power cable has the advantages of lightness in weight, simplicity in construction, smallness in dielectric loss besides its easy operation and antichemical corrosion properties. It can also be laid with no limitation of level difference along the route.

The cable is suitable to be installed in transmission and distribution lines of rated voltage from 6～35kV.

- Standard:

The cable is produced according to the standard GB/T12706—2002 which is equivalent to IEC60502-1997.

- Applications Feature:

  - Max. rated temperature of the cable conductor is 90℃.

b. Max. short circuit temperature of the cable conductor shall not exceed 250℃.(duration not exceeding 5s)

c. The rated voltage (Uo) are divided into two classes according to the earthing time. (see Table 1).

表1

The first class of cable: suitable for one single-phase earthing-block time does not exceed one minute each time. Max. time not exceed 8 hours, and not exceed 125 hours in all one year.

The second class of cable: suitable for more the earthing-block time and more better insulated performance.

d. The ambient temperature shall not be lower than 0℃ and the cable shall not be restricted by the difference of the level at installation and not preheat.

Min. bending radius during installation:

Single core cable: 20（D+d）±5% mm

Multi-core cable: 15（D+d）±5% mm

Where: D—the actual outer diameter of the cable          mm

d—the actual outer diameter of the conductor       mm

| Rated voltage between phases (U) | Max. voltage of equipment | Rated power frequency voltage between conductor and screen or metal sheath（U0） |  |
| --- | --- | --- | --- |
|  |  | First class of cable | Second class of cable |
| 6 10 15 20 35 | 7.2 12 17.5 24 42 | 3.6 6.0 8.7 12.0 21.0 | 6.0 8.7 12.0 18.0 26 |

3.  XLPE Cable’s Type and Main Application:

Table 2

| Type |  | Name | Maiin Application |
| --- | --- | --- | --- |
| Cu. Core | Al. Core |  |  |
| YJV YJY ZR-YJV ZR-YJY | YJLV YJLY ZR-YJLV ZR-YJLY | XLPE insulated PVC or PE sheathed power cable Flame retardant XLPE insulated PVC or PE sheathed power cable | For laying indoor, tunnel, ditch and conduits, as well as in loose soil, unable to bear external mechanical force, but bear the traction force during laid. |
| YJV22 YJV23 ZR-YJV22 ZR-YJV23 | YJLV22 YJLV23 ZR-YJLV22 ZR-YJLV23 | XLPE insulated steel tape armored PVC or PE sheathed power cable Flame retardant XLPE insulated steel tape armored PVC or PE sheathed power cable | For laying indoor, tunnel, ditch and underground, able to bear external mechanical forces, but unable to bear heavy pulling force. |
| YJV32 YJV33 ZR-YJV32 ZR-YJV33 | YJLV32 YJLV33 ZR-YJLV32 ZR-YJLV33 | XLPE insulated thin steel wire armored PVC or PE sheathed power cable Flame retardant XLPE insulated thin steel wire armored PVC or PE sheathed power cable | For laying in shaft, under water and soil, that has large difference of level, able to bear external mechanical forces and moderate pulling force. |
| YJV42 YJV43 ZR-YJV42 ZR-YJV43 | YJLV42 YJLV43 ZR-YJLV42 ZR-YJLV43 | XLPE insulated thick steel wire armored PVC or PE sheathed power cable Flame retardant XLPE insulated thick steel wire armored PVC or PE sheathed power cable | For laying in water and seabed, able to bear heavier positive pressure and pulling force. |

Note:

a. Except for the above mentioned cables, our company can also produce low smoke low (or free from) halogen, low smoke non-halogen XLPE insulated power cable.

b. Except the above mentioned cable types, our company can also produce waterproof power cable.

  - Scope for our XLPE cables:

Table 3

| Rated Voltage Cross-section mm2 No. of Cores | First class | 3.6/6 | 6/10 (6.35/11) | 8.7/15 | 12/20 (12.7/22) | 18/30 (19/33) | 21/25 |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Second class | 6/6 | 8.7/10 | 12/15 | 18/20 | - | 26/35 |
| 1 Core |  | 25-1200 | 25-1200 | 35-1200 | 50-1200 | 50-1200 | 50-1200 |
| 3 Cores |  | 25-400 | 25-400 | 35-400 | 50-300 | 50-300 | 50-300 |

  - Refer to Table 4-Table 15 about the dimension of the cable.

Refer to fig1-fig3 about the construction of cable.

Fig.1

Fig.3

3.6/6 kV Single Core XLPE Insulated Power Cable

Table  4

| Nominal Cross- Section | Nominal Thickness of Insulation | Single Core |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | YJV YJLV ZR-YJV ZR-YJLV |  |  | YJV32 YJLV32 ZR-YJV32 ZR-YJLV32 |  |  | YJV42 YJLV42 ZR-YJV42 ZR-YJLV42 |  |  |
|  |  | Approx. Overall Diameter of Cable | Approx. Weight of Cable |  | Approx. Overall Diameter of Cable | Approx. Weight of Cable |  | Approx. Overall Diameter of Cable | Approx. Weight of able |  |
|  |  |  | Cu | Al |  | Cu | Al |  | Cu | Al |
| mm2 | mm | mm | kg/km |  | mm | kg/km |  | mm | kg/km |  |
| 25 | 2.5 | 19 | 576 | 421 | 25 | 1565 | 1410 | 30 | 2599 | 2444 |
| 35 | 2.5 | 20 | 695 | 479 | 26 | 1727 | 1510 | 31 | 2799 | 2582 |
| 50 | 2.5 | 21 | 860 | 550 | 27 | 1955 | 1645 | 33 | 3309 | 2782 |
| 70 | 2.5 | 23 | 1081 | 648 | 29 | 2269 | 1836 | 35 | 3460 | 3027 |
| 95 | 2.5 | 24 | 1350 | 762 | 30 | 2609 | 2021 | 36 | 3878 | 3290 |
| 120 | 2.5 | 26 | 1640 | 897 | 32 | 2948 | 2205 | 38 | 4258 | 3515 |
| 150 | 2.5 | 27 | 1947 | 1019 | 33 | 3670 | 2741 | 40 | 4721 | 3793 |
| 185 | 2.5 | 29 | 2302 | 1156 | 36 | 4115 | 2970 | 41 | 5214 | 4068 |
| 240 | 2.6 | 32 | 2886 | 1400 | 38 | 4828 | 3342 | 44 | 5998 | 4512 |
| 300 | 2.8 | 35 | 3483 | 1626 | 41 | 5616 | 3759 | 47 | 6865 | 5008 |
| 400 | 3.0 | 38 | 4477 | 2001 | 45 | 7611 | 5135 | 52 | 8400 | 5924 |
| 500 | 3.2 | 41 | 5452 | 2357 | 49 | 8986 | 5891 | 56 | 9843 | 6748 |
| 630 | 3.2 | 47 | 6994 | 3094 | 56 | 10298 | 6399 | 60 | 11433 | 7533 |
| 800 | 3.2 | 51 | 8650 | 3690 | 62 | 12467 | 7507 | 64 | 13463 | 8503 |
| 1000 | 3.2 | 57 | 10726 | 4427 | 68 | 14928 | 8550 | 70 | 15988 | 9572 |
| 1200 | 3.2 | 61 | 12671 | 5131 | 72 | 17169 | 9487 | 73 | 18284 | 10626 |

6/6、6/10(6.35/11)kV  Single Core XLPE Insulated Power Cable:

Table  5

| Nominal Cross-section of Conductor | Nominal Thickness of Insulation | Single Core |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | YJV YJLV ZR-YJV ZR-YJLV |  |  | YJV32 YJLV32 ZR-YJV32 ZR-YJLV32 |  |  | YJV42 YJLV42 ZR-YJV42 ZR-YJLV42 |  |  |
|  |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  |
|  |  |  | Cu | Al |  | Cu. | Al. |  | Cu | Al |
| mm2 | mm | mm | kg/km |  | mm | kg/km |  | mm | kg/km |  |
| 25 | 3.4 | 20 | 598 | 443 | 27 | 1439 | 1283 | 32 | 2832 | 2677 |
| 35 | 3.4 | 22 | 719 | 502 | 28 | 1604 | 1387 | 34 | 3049 | 2833 |
| 50 | 3.4 | 23 | 884 | 575 | 29 | 1828 | 1518 | 35 | 3332 | 3023 |
| 70 | 3.4 | 24 | 1097 | 664 | 31 | 2091 | 1657 | 37 | 3721 | 3288 |
| 95 | 3.4 | 26 | 1378 | 790 | 32 | 2674 | 2086 | 38 | 4128 | 3540 |
| 120 | 3.4 | 28 | 1658 | 916 | 34 | 3051 | 2308 | 40 | 4529 | 3786 |
| 150 | 3.4 | 30 | 1967 | 1038 | 36 | 3517 | 2589 | 42 | 4981 | 4052 |
| 185 | 3.4 | 31 | 2335 | 1190 | 38 | 3967 | 2822 | 43 | 5496 | 4351 |
| 240 | 3.4 | 34 | 2908 | 1423 | 40 | 5023 | 3538 | 46 | 6260 | 4775 |
| 300 | 3.4 | 36 | 3507 | 1650 | 42 | 5774 | 3917 | 48 | 7051 | 5194 |
| 400 | 3.4 | 39 | 4503 | 2027 | 47 | 6929 | 4453 | 53 | 8531 | 6055 |
| 500 | 3.4 | 42 | 5479 | 2384 | 50 | 8080 | 4985 | 56 | 9913 | 6818 |
| 630 | 3.4 | 48 | 7029 | 3129 | 58 | 10585 | 6685 | 60 | 11531 | 7631 |
| 800 | 3.4 | 52 | 8708 | 3740 | 62 | 12506 | 7546 | 64 | 13501 | 8541 |
| 1000 | 3.4 | 58 | 10764 | 4465 | 68 | 15034 | 8592 | 70 | 16031 | 9613 |
| 1200 | 3.4 | 62 | 12712 | 5171 | 72 | 17214 | 9594 | 74 | 18361 | 10703 |

8.7/10、8.7/15kV  Single Core XLPE Insulated Power Cable

Table  6

| Nominal Cross-section of Conductor | Nominal Thickness of Insulation | Single Core |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | YJV YJLV ZR-YJV ZR-YJLV |  |  | YJV32 YJLV32 ZR-YJV32 ZR-YJLV32 |  |  | YJV42 YJLV42 ZR-YJV42 ZR-YJLV42 |  |  |
|  |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  |
|  |  |  | Cu | Al |  | Cu. | Al. |  | Cu | Al |
| mm2 | mm | mm | kg/km |  | mm | kg/km |  | mm | kg/km |  |
| 25 | 4.5 | 23 | 680 | 525 | 30 | 1616 | 1461 | 35 | 3140 | 2986 |
| 35 | 4.5 | 24 | 804 | 587 | 31 | 1786 | 1570 | 36 | 3348 | 3131 |
| 50 | 4.5 | 25 | 984 | 674 | 32 | 2015 | 1706 | 37 | 3651 | 3341 |
| 70 | 4.5 | 27 | 1201 | 768 | 34 | 2515 | 2082 | 39 | 4048 | 3614 |
| 95 | 4.5 | 29 | 1490 | 902 | 37 | 2906 | 2318 | 41 | 4461 | 3873 |
| 120 | 4.5 | 30 | 1765 | 1022 | 38 | 3260 | 2518 | 42 | 4868 | 4125 |
| 150 | 4.5 | 32 | 2091 | 1162 | 41 | 3735 | 2805 | 44 | 5326 | 4398 |
| 185 | 4.5 | 34 | 2452 | 1307 | 44 | 4582 | 3437 | 46 | 5849 | 4704 |
| 240 | 4.5 | 36 | 3034 | 1548 | 46 | 5295 | 3810 | 48 | 6602 | 5116 |
| 300 | 4.5 | 39 | 3672 | 1815 | 48 | 6035 | 4178 | 50 | 7421 | 5564 |
| 400 | 4.5 | 42 | 4646 | 2170 | 51 | 7200 | 4724 | 55 | 8920 | 6444 |
| 500 | 4.5 | 45 | 5651 | 2556 | 56 | 8995 | 5900 | 59 | 10317 | 7222 |
| 630 | 4.5 | 51 | 7240 | 3340 | 61 | 10964 | 7065 | 63 | 11924 | 8024 |
| 800 | 4.5 | 54 | 8900 | 3940 | 64 | 12870 | 7910 | 66 | 13954 | 8994 |
| 1000 | 4.5 | 60 | 11005 | 4700 | 70 | 15430 | 8900 | 72 | 16507 | 10083 |
| 1200 | 4.5 | 64 | 12970 | 5420 | 74 | 17620 | 10000 | 76 | 18820 | 11156 |

12/20(12.7/22)kV  Single Core XLPE Insulated Power Cable;

Table  7

| Nominal Cross-section of Conductor | Nominal Thickness of Insulation | Single Core |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | YJV YJLV ZR-YJV ZR-YJLV |  |  | YJV32 YJLV32 ZR-YJV32 ZR-YJLV32 |  |  | YJV42 YJLV42 ZR-YJV42 ZR-YJLV42 |  |  |
|  |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  |
|  |  |  | Cu | Al |  | Cu. | Al. |  | Cu | Al |
| mm2 | mm | mm | kg/km |  | mm | kg/km |  | mm | kg/km |  |
| 35 | 5.5 | 27 | 979 | 762 | 35 | 2335 | 2118 | 39 | 3695 | 3479 |
| 50 | 5.5 | 29 | 1155 | 846 | 36 | 2598 | 2288 | 40 | 4005 | 3696 |
| 70 | 5.5 | 30 | 1393 | 959 | 38 | 2884 | 2450 | 42 | 4393 | 3959 |
| 95 | 5.5 | 32 | 1681 | 1093 | 40 | 3256 | 2668 | 44 | 4831 | 4243 |
| 120 | 5.5 | 34 | 1979 | 1236 | 42 | 3620 | 2877 | 45 | 5226 | 4483 |
| 150 | 5.5 | 35 | 2301 | 1373 | 45 | 4518 | 3589 | 47 | 5710 | 4782 |
| 185 | 5.5 | 38 | 2718 | 1573 | 47 | 4981 | 3836 | 48 | 6220 | 5075 |
| 240 | 5.5 | 40 | 3302 | 1817 | 49 | 5728 | 4243 | 51 | 7003 | 5518 |
| 300 | 5.5 | 43 | 3941 | 2084 | 52 | 6503 | 4646 | 53 | 7833 | 5976 |
| 400 | 5.5 | 45 | 4931 | 2455 | 56 | 8303 | 5827 | 57 | 9234 | 6808 |
| 500 | 5.5 | 48 | 5956 | 2861 | 59 | 9543 | 6448 | 61 | 10696 | 7601 |
| 630 | 5.5 | 53 | 7443 | 3543 | 63 | 11293 | 7393 | 65 | 12315 | 8416 |
| 800 | 5.5 | 56 | 9114 | 4154 | 66 | 13241 | 8281 | 68 | 14263 | 9303 |
| 1000 | 5.5 | 62 | 11212 | 4902 | 73 | 15783 | 9330 | 75 | 16970 | 10438 |
| 1200 | 5.5 | 66 | 13107 | 5636 | 77 | 17990 | 10360 | 78 | 19193 | 11525 |

18/20、18/30(19/33)kV Single Core XLPE Insulated Power Cable:

Table 8

| Nominal Cross-section of Conductor | Nominal Thickness of Insulation | Single Core |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | YJV YJLV ZR-YJV ZR-YJLV |  |  | YJV32 YJLV32 ZR-YJV32 ZR-YJLV32 |  |  | YJV42 YJLV42 ZR-YJV42 ZR-YJLV42 |  |  |
|  |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  |
|  |  |  | Cu | Al |  | Cu. | Al. |  | Cu | Al |
| mm2 | mm | mm | kg/km |  | mm | kg/km |  | mm | kg/km |  |
| 50 | 8.0 | 35 | 1562 | 1253 | 44 | 3733 | 3423 | 47 | 4979 | 4670 |
| 70 | 8.0 | 37 | 1838 | 1405 | 45 | 4089 | 3656 | 49 | 5406 | 4972 |
| 95 | 8.0 | 39 | 2138 | 1550 | 47 | 4479 | 3819 | 51 | 5865 | 5276 |
| 120 | 8.0 | 40 | 2446 | 1703 | 50 | 5456 | 4713 | 52 | 6275 | 5532 |
| 150 | 8.0 | 42 | 2791 | 1863 | 52 | 5934 | 5006 | 54 | 6781 | 5852 |
| 185 | 8.0 | 44 | 3200 | 2054 | 54 | 6458 | 5313 | 56 | 7308 | 6163 |
| 240 | 8.0 | 46 | 3797 | 2312 | 56 | 7208 | 5722 | 58 | 8119 | 6634 |
| 300 | 8.0 | 48 | 4461 | 2604 | 58 | 8028 | 6171 | 60 | 8977 | 7120 |
| 400 | 8.0 | 52 | 5531 | 3055 | 62 | 9325 | 6849 | 64 | 10328 | 7852 |
| 500 | 8.0 | 55 | 6659 | 3564 | 66 | 10712 | 7617 | 68 | 11778 | 8683 |
| 630 | 8.0 | 59 | 8017 | 4117 | 69 | 12309 | 8410 | 71 | 13443 | 9537 |
| 800 | 8.0 | 62 | 9707 | 4747 | 72 | 14275 | 9315 | 74 | 15306 | 10400 |
| 1000 | 8.0 | 68 | 11891 | 5566 | 79 | 16844 | 10439 | 80 | 18092 | 11648 |
| 1200 | 8.0 | 72 | 13904 | 6339 | 83 | 19153 | 11446 | 84 | 20492 | 12707 |

21/35kV  Single Core XLPE Insulated Power Cable:

Table  9

| Nominal Cross-section of Conductor | Nominal Thickness of Insulation | Single Core |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | YJV YJLV ZR-YJV ZR-YJLV |  |  | YJV32 YJLV32 ZR-YJV32 ZR-YJLV32 |  |  | YJV42 YJLV42 ZR-YJV42 ZR-YJLV42 |  |  |
|  |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  |
|  |  |  | Cu | Al |  | Cu. | Al. |  | Cu | Al |
| mm2 | mm | mm | kg/km |  | mm | kg/km |  | mm | kg/km |  |
| 50 | 9.3 | 37 | 1609 | 1360 | 47 | 3779 | 3469 | 50 | 5414 | 5104 |
| 70 | 9.3 | 38 | 1850 | 1417 | 48 | 4112 | 3679 | 52 | 5849 | 5416 |
| 95 | 9.3 | 40 | 2193 | 1605 | 50 | 4523 | 3935 | 54 | 6317 | 5729 |
| 120 | 9.3 | 42 | 2498 | 1756 | 52 | 4944 | 4202 | 55 | 6734 | 5991 |
| 150 | 9.3 | 44 | 2839 | 1910 | 54 | 5510 | 4581 | 57 | 7248 | 6320 |
| 185 | 9.3 | 45 | 3248 | 2102 | 56 | 6634 | 5489 | 59 | 7782 | 6637 |
| 240 | 9.3 | 48 | 3881 | 2395 | 60 | 7447 | 5961 | 61 | 8604 | 7119 |
| 300 | 9.3 | 50 | 4529 | 2672 | 63 | 8308 | 6451 | 63 | 9473 | 7616 |
| 400 | 9.3 | 53 | 5570 | 3094 | 65 | 9512 | 7036 | 67 | 10840 | 8365 |
| 500 | 9.3 | 55 | 6690 | 3595 | 68 | 10756 | 7661 | 73 | 12679 | 9584 |
| 630 | 9.3 | 64 | 8480 | 4581 | 74 | 13126 | 9226 | 77 | 14339 | 10439 |
| 800 | 9.3 | 67 | 10220 | 5265 | 79 | 15248 | 10288 | 81 | 16495 | 11535 |
| 1000 | 9.3 | 74 | 12420 | 6100 | 84 | 17872 | 11392 | 87 | 19188 | 12732 |
| 1200 | 9.3 | 77 | 14451 | 6883 | 88 | 20129 | 12474 | 91 | 21565 | 13869 |

26/35kV Single Core XLPE Insulated Power Cable:

Table 10

| Nominal Cross-section of Conductor | Nominal Thickness of Insulation | Single Core |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | YJV YJLV ZR-YJV ZR-YJLV |  |  | YJV32 YJLV32 ZR-YJV32 ZR-YJLV32 |  |  | YJV42 YJLV42 ZR-YJV42 ZR-YJLV42 |  |  |
|  |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  |
|  |  |  | Cu | Al |  | Cu. | Al. |  | Cu | Al |
| mm2 | mm | mm | kg/km |  | mm | kg/km |  | mm | kg/km |  |
| 50 | 10.5 | 39 | 1758 | 1449 | 48 | 4083 | 3773 | 53 | 5885 | 5576 |
| 70 | 10.5 | 41 | 2038 | 1604 | 50 | 4422 | 3989 | 55 | 6329 | 5896 |
| 95 | 10.5 | 43 | 2355 | 1767 | 52 | 4840 | 4252 | 57 | 6781 | 6193 |
| 120 | 10.5 | 44 | 2666 | 1923 | 53 | 5269 | 4526 | 58 | 7230 | 6487 |
| 150 | 10.5 | 46 | 3031 | 2103 | 57 | 6497 | 5569 | 60 | 7727 | 6799 |
| 185 | 10.5 | 48 | 3427 | 2282 | 59 | 7007 | 5861 | 62 | 8295 | 7150 |
| 240 | 10.5 | 50 | 4070 | 2584 | 62 | 7856 | 6371 | 64 | 9130 | 7644 |
| 300 | 10.5 | 53 | 4748 | 2891 | 64 | 8676 | 6819 | 66 | 9982 | 8125 |
| 400 | 10.5 | 56 | 5801 | 3325 | 67 | 9917 | 7441 | 70 | 11365 | 8889 |
| 500 | 10.5 | 59 | 6623 | 4076 | 70 | 11365 | 8101 | 76 | 13216 | 10121 |
| 630 | 10.5 | 67 | 8793 | 4894 | 78 | 13634 | 9734 | 81 | 14894 | 10994 |
| 800 | 10.5 | 70 | 10567 | 5607 | 82 | 15776 | 10816 | 84 | 17076 | 12116 |
| 1000 | 10.5 | 77 | 12798 | 6462 | 88 | 18403 | 11979 | 90 | 19759 | 13296 |
| 1200 | 10.5 | 80 | 14840 | 7265 | 92 | 20744 | 13081 | 94 | 22195 | 14493 |

3.6/6kV  Three Cores XLPE Insulated Power Cable:

Table 11

| Nominal Cross-section of Conductor | Nominal Thickness of Insulation | Three Cores |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | YJV YJLV ZR-YJV ZR-YJLV |  |  |  | YJV22 YJLV22 ZR-YJV22ZR-YJLV22 |  |  | YJV32 YJLV32 ZR-YJV32 ZR-YJLV32 |  |  |  | YJV42 YJLV42 ZR-YJV42 ZR-YJLV42 |  |  |
|  |  | Approx. Overall Diameter | Approx. Weight of Cable |  |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  |  | Approx. Overall Diameter | Approx. Weight of Cable |  |
|  |  |  | Cu | Al |  |  | Cu. | Al. |  | Cu | Al |  |  | Cu. | Al. |
| mm2 | mm | mm | kg/km |  |  | mm | kg/km |  | mm | kg/km |  |  | mm | kg/km |  |
| 25 | 2.5 | 40 | 1895 |  | 1430 | 46 | 2945 | 2480 | 49 | 4246 |  | 3781 | 49.2 | 5289 | 4821 |
| 35 | 2.5 | 43 | 2293 |  | 1642 | 49 | 3390 | 2739 | 52 | 4770 |  | 4119 | 51.6 | 5798 | 5143 |
| 50 | 2.5 | 46 | 2812 |  | 1881 | 52 | 4065 | 3135 | 57 | 6194 |  | 5263 | 54.6 | 6685 | 5749 |
| 70 | 2.5 | 49 | 3508 |  | 2205 | 55 | 4816 | 3513 | 60 | 7092 |  | 5790 | 58.6 | 7681 | 6371 |
| 95 | 2.5 | 53 | 4402 |  | 2635 | 60 | 5897 | 4129 | 64 | 8763 |  | 6495 | 62.3 | 8887 | 7109 |
| 120 | 2.5 | 57 | 5317 |  | 3087 | 63 | 6844 | 4611 | 68 | 9422 |  | 7190 | 65.5 | 9969 | 7723 |
| 150 | 2.5 | 61 | 6300 |  | 3518 | 67 | 7973 | 5182 | 71 | 10667 |  | 7876 | 69.1 | 11320 | 8512 |
| 185 | 2.5 | 63 | 7319 |  | 3877 | 71 | 9281 | 5838 | 76 | 12113 |  | 8671 | 72.8 | 12711 | 9248 |
| 240 | 2.6 | 70 | 9218 |  | 4753 | 77 | 11229 | 6763 | 81 | 14361 |  | 9895 | 78.4 | 15010 | 10518 |
| 300 | 2.6 | 75 | 11159 |  | 5977 | 83 | 14106 | 8524 | 87 | 16632 |  | 11050 | 85.4 | 17783 | 12168 |

6/6、6/10(6.35/11)kV  Three Cores XLPE Insulated Power Cable

Table 12

| Nominal Cross-section of Conductor | Nominal Thickness of Insulation | Three Cores |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | YJV YJLV ZR-YJV ZR-YJLV |  |  | YJV22 YJLV22 ZR-YJV22 ZR-YJLV22 |  |  | YJV32 YJLV32 ZR-YJV32 ZR-YJLV32 |  |  | YJV42 YJLV42 ZR-YJV42 ZR-YJLV42 |  |  |
|  |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  |
|  |  |  | Cu | Al |  | Cu. | Al. |  | Cu | Al. |  | Cu. | Al. |
| mm2 | mm | mm | kg/km |  | mm | kg/km |  | mm | kg/km |  | mm | kg/km |  |
| 25 | 3.4 | 42 | 1895 | 1430 | 47 | 3010 | 2544 | 50 | 4337 | 3872 | 54 | 5902 | 5452 |
| 35 | 3.4 | 44 | 2293 | 1640 | 50 | 3490 | 2847 | 53 | 4863 | 4214 | 56 | 6444 | 5789 |
| 50 | 3.4 | 46 | 2812 | 1881 | 53 | 4135 | 3205 | 58 | 6302 | 5371 | 59 | 7349 | 6413 |
| 70 | 3.4 | 50 | 3508 | 2205 | 56 | 4958 | 3655 | 61 | 7177 | 5875 | 63 | 8345 | 7035 |
| 95 | 3.4 | 54 | 4402 | 2635 | 61 | 5874 | 4206 | 65 | 8431 | 6663 | 67 | 9570 | 7792 |
| 120 | 3.4 | 58 | 5319 | 3087 | 64 | 6969 | 4736 | 69 | 9559 | 7326 | 70 | 10671 | 8425 |
| 150 | 3.4 | 62 | 6309 | 3518 | 69 | 8161 | 5370 | 73 | 10873 | 8246 | 74 | 12044 | 9237 |
| 185 | 3.4 | 65 | 7319 | 3877 | 72 | 9417 | 5975 | 76 | 12256 | 8814 | 77 | 13486 | 10023 |
| 240 | 3.4 | 71 | 9218 | 4753 | 78 | 11340 | 6874 | 82 | 14509 | 10044 | 84 | 16036 | 11544 |
| 300 | 3.4 | 75 | 11159 | 5577 | 84 | 14247 | 8665 | 88 | 16821 | 11239 | 88 | 18340 | 12725 |

8.7/10、8.7/15kV  Three Cores XLPE Insulated Power Cable

Table 13

| Nominal Cross-section of Conductor | Nominal Thickness of Insulation | Three Cores |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | YJV YJLV ZR-YJV ZR-YJLV |  |  | YJV22 YJLV22 ZR-YJV22 ZR-YJLV22 |  |  | YJV32 YJLV32 ZR-YJV32 ZR-YJLV32 |  |  | YJV42 YJLV42 ZR-YJV42 ZR-YJLV42 |  |  |
|  |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  |
|  |  |  | Cu | Al |  | Cu. | Al. |  | Cu | Al. |  | Cu. | Al. |
| mm2 | mm | mm | kg/km |  | mm | kg/km |  | mm | kg/km |  | mm | kg/km |  |
| 25 | 4.5 | 50 | 2537 | 2072 | 53 | 3500 | 3035 | 60 | 6058 | 5593 | 59 | 6775 | 6287 |
| 35 | 4.5 | 53 | 2985 | 2334 | 55 | 3980 | 3329 | 63 | 6661 | 6010 | 62 | 7296 | 6641 |
| 50 | 4.5 | 55 | 3529 | 2598 | 58 | 4679 | 3748 | 66 | 7456 | 6525 | 64 | 8122 | 7186 |
| 70 | 4.5 | 58 | 4197 | 2895 | 61 | 5410 | 4107 | 69 | 8376 | 7074 | 68 | 9247 | 7936 |
| 95 | 4.5 | 63 | 5230 | 3462 | 66 | 6567 | 4799 | 73 | 9657 | 7890 | 72 | 10500 | 8722 |
| 120 | 4.5 | 66 | 6120 | 3888 | 70 | 7541 | 5308 | 76 | 10834 | 8602 | 75 | 11624 | 9378 |
| 150 | 4.5 | 70 | 7207 | 4416 | 73 | 8674 | 5883 | 81 | 12160 | 9369 | 79 | 13024 | 10216 |
| 185 | 4.5 | 74 | 8378 | 4935 | 77 | 9991 | 6547 | 85 | 13661 | 10219 | 84 | 14758 | 11295 |
| 240 | 4.5 | 79 | 10177 | 5712 | 84 | 12887 | 8421 | 91 | 15992 | 11527 | 89 | 16951 | 12459 |
| 300 | 4.5 | 84 | 12159 | 6577 | 89 | 14974 | 9392 | 96 | 18262 | 12680 | 94 | 19436 | 13820 |

12/20(12.7/22)kV  Three Cores XLPE Insulated Power Cable:

Table 14

| Nominal Cross-section of Conductor | Nominal Thickness of Insulation | Three Cores |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | YJV YJLV ZR-YJV ZR-YJLV |  |  | YJV22 YJLV22 ZR-YJV22 ZR-YJLV22 |  |  | YJV32 YJLV32 ZR-YJV32 ZR-YJLV32 |  |  |  | YJV42 YJLV42 ZR-YJV42 ZR-YJLV42 |  |  |  |
|  |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  |  | Approx. Overall Diameter | Approx. Weight of Cable |  |  |
|  |  |  | Cu | Al |  | Cu. | Al. |  | Cu | Al. |  |  | Cu. | Al. |  |
| mm2 | mm | mm | kg/km |  | mm | kg/km |  | mm | kg/km |  |  | mm | kg/km |  |  |
| 35 | 5.5 | 57 | 3348 | 2096 | 63 | 4840 | 4189 | 68 | 7430 |  | 6752 | 68 | 8229 |  | 7574 |
| 50 | 5.5 | 60 | 3904 | 2973 | 66 | 5463 | 4532 | 70 | 8139 |  | 7200 | 71 | 9181 |  | 8245 |
| 70 | 5.5 | 63 | 4623 | 3321 | 69 | 6346 | 5044 | 74 | 9133 |  | 7831 | 74 | 10234 |  | 8924 |
| 95 | 5.5 | 67 | 5593 | 3825 | 74 | 7457 | 5689 | 78 | 10450 |  | 8682 | 78 | 11517 |  | 9739 |
| 120 | 5.5 | 71 | 6495 | 4262 | 77 | 8439 | 6227 | 82 | 11612 |  | 9371 | 82 | 12926 |  | 10680 |
| 150 | 5.5 | 74 | 2637 | 4846 | 82 | 10555 | 7764 | 86 | 12482 |  | 10191 | 86 | 14258 |  | 11450 |
| 185 | 5.5 | 78 | 8803 | 5361 | 86 | 11925 | 8483 | 89 | 14540 |  | 11098 | 90 | 15874 |  | 12412 |
| 240 | 5.5 | 84 | 10729 | 6263 | 92 | 13959 | 9494 | 95 | 16751 |  | 12785 | 95 | 18209 |  | 13717 |
| 300 | 5.5 | 89 | 12723 | 7141 | 97 | 16314 | 10731 | 101 | 19242 |  | 13660 | 100 | 20632 |  | 15017 |

26/35kV  Three Cores XLPE Insulated Power Cable:

Table 15

| Nominal Cross-section of Conductor | Nominal Thickness of Insulation | Three Cores |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | YJV YJLV ZR-YJV ZR-YJLV |  |  | YJV22 YJLV22 ZR-YJV22 ZR-YJLV22 |  |  | YJV32 YJLV32 ZR-YJV32 ZR-YJLV32 |  |  | YJV42 YJLV42 ZR-YJV42 ZR-YJLV42 |  |  |
|  |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  | Approx. Overall Diameter | Approx. Weight of Cable |  |
|  |  |  | Cu | Al |  | Cu. | Al. |  | Cu | Al. |  | Cu. | Al. |
| mm2 | mm | mm | kg/km |  | mm | kg/km |  | mm | kg/km |  | mm | kg/km |  |
| 50 | 10.5 | 84 | 6000 | 5078 | 92 | 9491 | 8569 | 91.6 | 10024 | 9088 | 94.9 | 13058 | 12122 |
| 70 | 10.5 | 88 | 6960 | 5643 | 96 | 10614 | 9298 | 95.5 | 11186 | 9876 | 98.8 | 14350 | 13040 |
| 95 | 10.5 | 92 | 7661 | 6150 | 100 | 11788 | 9987 | 99.7 | 12537 | 10759 | 103.0 | 15842 | 14064 |
| 120 | 10.5 | 95 | 9203 | 6958 | 103 | 13216 | 10791 | 102.9 | 13698 | 11452 | 106.4 | 17156 | 14910 |
| 150 | 10.5 | 98 | 10349 | 7535 | 107 | 14512 | 11698 | 100.8 | 15120 | 12312 | 110.1 | 18057 | 15849 |
| 185 | 10.5 | 102 | 11612 | 8181 | 111 | 15981 | 12550 | 110.4 | 16620 | 13158 | 113.7 | 20276 | 16814 |
| 240 | 10.5 | 107 | 13594 | 9117 | 116 | 18219 | 13742 | 115.3 | 18871 | 14379 | 118.4 | 22641 | 18149 |
| 300 | 10.5 | 112 | 15757 | 10134 | 121 | 20703 | 15080 | 120.1 | 21222 | 15606 | 123.2 | 25158 | 19542 |

6.   Main Technical Parameters of Cable:

a.  D.C. resistance: Conductor resistance of completed cable at  20℃ per kilometer is not more than values in Table 16.

Table 16

| Nominal Cross-section mm2 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Cu. Core | 0.727 | 0.524 | 0.387 | 0.268 | 0.193 | 0.153 | 0.124 | 0.0991 |
| Al. Core | 1.20 | 0.868 | 0.641 | 0.443 | 0.320 | 0.253 | 0.206 | 0.164 |

| Nominal Cross-section mm2 | 240 | 300 | 400 | 500 | 630 | 800 | 1000 | 1200 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Cu. Core | 0.0754 | 0.0601 | 0.0470 | 0.0366 | 0.0283 | 0.0211 | 0.0176 | 0.0151 |
| Al. Core | 0.125 | 0.100 | 0.0778 | 0.0605 | 0.0469 | 0.0367 | 0.0291 | 0.0247 |

- Voltage Test and Partial Discharge Test (see Table 17)

Table  17

| Rated Voltage Item |  |  | 3.6/6 | 6/6 6/10 | 8.7/10 8.7/15 | 12/20 | 18/20 18/30 | 21/35 | 26/35 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Voltage Test | Test Voltage kV | 12.5 | 21 | 30.5 | 42 | 63 | 73.5 | 91 |
|  |  | Test Period min | 5 | 5 | 5 | 5 | 5 | 5 | 5 |
| 2 | Partial Discharge Test | Test Voltage kV | 6 | 10 | 15 | 20 | 31 | 33 | 45 |
|  |  | Discharge Magnitude <pC | 20 | 10 | 10 | 10 | 10 | 5 | 5 |

C.   Rated  short Circuit Current of Cu./Al. Conductor (see Table 18):

The short circuit current in conductor at 1 second , kA

| Cross-section of Conductor mm2 |  | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor Short Circuit Temperature is 250℃ | Cu | 3.69 | 5.15 | 7.31 | 10.2 | 13.8 | 17.4 | 21.7 | 26.7 |
|  | Al | 2.42 | 3.37 | 4.79 | 6.68 | 9.03 | 11.4 | 14.2 | 17.4 |

| Cross-section of Conductor mm2 |  | 240 | 300 | 400 | 500 | 630 | 800 | 1000 | 1200 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor Short Circuit Temperature is 250℃ | Cu | 34.6 | 43.1 | 57.4 | 71.7 | 88.8 | 114.5 | 143.1 | 171.7 |
|  | Al | 22.6 | 28.2 | 37.6 | 47.0 | 58.0 | 75.0 | 93.7 | 112.4 |

- Referential Current Rating:

  - Refer to Table 19-Table 24 about the referential current rating.

  - Refer to Table 25-Table 26 about the correct factors rated current of XLPE cable at different temperature.

  - Refer to Table 27 about the correct factors for rated current of XLPE cable with different soil coefficient of thermal resistivity.

- Delivery Length:

  - The length of each supply cable shall be generally not less than 100m.

  - Short cable is permitted to supply yet not shorter than 50m for each and their quantity shall not exceed 10% of the total supply length. The measuring tolerance shall not be more than ±0.5%.

  - Non-standard supply length may be allowed if both parties agree.

- Designation of Ordering:

For example: ordering of 10km of  8.7/10kV 3-core, 240mm2 copper conductor, XLPE insulated, PVC sheathed and steel tape armored power cable.

The designation shall be: 8.7/10kV  YJV22  3×240mm2  10km  GB/T12706-2002

Attention: XLPE insulated power cable should be used with special XLPE cable terminal and joint together

The current rating for single core XLPE insulated cable. （A）

Table 19

| Type | YJV YJLV YJY YJLY |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Voltage | 3.6/6-12/20(12.7/22)kV |  |  |  |  |
| Arrangement | Trefoil (in contact) |  |  |  |  |
| Installation Condition | In Air | Underground （k.m/w） |  |  |  |
|  |  | ρw |  | ρD(moving the moisture out) |  |
|  |  | 1.0 | 2.5 | 3.0 | 3.5 |
| Cross-sectional Area（mm2） | Cu. Al. | Cu. Al. | Cu. Al. | Cu. Al. | Cu. Al. |
| 25 35 50 70 95 | 140 110 170 135 205 160 260 200 315 245 | 150 115 180 135 215 160 265 200 315 240 | 130 99 155 115 180 135 220 165 265 200 | 120 89 140 105 170 125 205 150 245 180 | 105 75 125 90 150 105 180 130 215 155 |
| 120 150 185 240 300 | 360 280 410 320 470 365 555 435 640 500 | 360 270 405 305 455 345 530 400 595 455 | 300 225 335 255 380 285 440 330 495 375 | 275 205 310 230 350 260 405 300 455 340 | 245 175 275 195 310 220 360 255 405 290 |
| 400 500 630 800 1000 | 745 585 855 680 980 790 1100 910 1230 1030 | 680 520 765 595 860 680 950 765 1040 850 | 560 430 630 490 710 555 785 625 850 695 | 515 385 585 440 655 500 725 565 785 625 | 460 330 520 375 580 430 645 485 700 535 |
| 1200 | 1320 1120 | 1100 910 | 900 745 | 830 670 | 735 575 |
| Conductor Temperature（℃） | 90 |  |  |  |  |
| Ambient Temperature（℃） | 40 | 25 |  |  |  |

Note: ρw— Soil thermal resistivity without moving the moisture out.

ρD— Soil thermal resistivity with moving the moisture out and making soil dried.

The current rating for single core XLPE insulated cable:

Table 20

| Type | YJV YJLV YJY YJLY |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Voltage | 3.6/6-12/20(12.7/22)kV |  |  |  |  |
| Arrange | Parallel（The distance between two cables is the diameter of the cable） |  |  |  |  |
| Installation | In Air | Underground（k.m/w） |  |  |  |
|  |  | ρw |  | ρD(moving the moisture out) |  |
|  |  | 1.0 | 2.5 | 3.0 | 3.5 |
| Cross-sectional Area（mm2） | Cu. Al. | Cu. Al. | Cu. Al. | Cu. Al. | Cu. Al. |
| 25 35 50 70 95 120 150 185 240 300 400 500 630 800 1000 1200 | 165 130 205 115 245 190 305 235 370 290 430 335 490 380 560 435 665 515 765 595 890 695 1030 810 1190 950 1370 1100 1540 1260 1670 1380 | 160 120 190 145 225 175 275 215 330 255 375 290 425 330 480 370 555 435 630 490 725 565 825 650 940 745 1050 850 1170 950 1250 1040 | 140 110 165 130 195 150 240 185 285 220 325 250 365 280 410 320 475 370 535 415 610 480 695 550 790 625 890 715 980 800 1050 870 | 135 105 160 125 190 150 235 180 280 215 315 245 355 275 400 310 460 360 520 405 595 465 680 535 770 610 865 695 950 780 1020 845 | 135 105 160 125 190 145 230 180 275 210 310 240 345 270 390 305 455 350 510 400 585 455 665 525 755 600 850 680 940 765 1000 830 |
| Conductor Temperature（℃） | 90 |  |  |  |  |
| Ambient Temperature（℃） | 40 | 25 |  |  |  |

Note: ρw— Soil thermal resistivity without moving the moisture out.

ρD— Soil thermal resistivity with moving the moisture out and making soil dried.

The current rating  for single core XLPE insulated cable (A):

Table 21

| Type | YJV YJLV YJY YJLY |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Voltage | 3.6/6-26/35（kV） |  |  |  |  |
| Arrangement | Trefoil (in contact) |  |  |  |  |
| Installation Condition | In Air | Underground （k.m/w） |  |  |  |
|  |  | ρw |  |  |  |
|  |  | 1.0 |  |  | 1.0 |
| Cross-sectional Area（mm2） | Cu. Al. | Cu. Al. | Cross-sectional Area（mm2） | Cu. Al. | Cu. Al. |
| 50 70 95 120 150 185 240 300 400 500 630 800 1000 1200 | 220 170 270 210 330 255 375 290 425 330 485 380 560 435 650 510 760 595 875 690 1000 800 1130 920 1250 1040 1350 1130 | 215 165 265 220 315 240 360 270 400 305 455 345 525 400 595 455 680 525 775 600 875 685 970 770 1060 860 1120 920 | 190 140 230 175 275 205 310 235 345 260 390 295 450 340 505 385 580 440 655 505 735 575 815 645 885 715 930 770 | 175 130 215 160 255 190 290 215 320 240 360 270 420 310 470 350 535 400 605 455 680 520 755 585 820 650 870 695 | 160 110 190 135 230 160 260 185 290 205 325 230 375 265 420 300 480 345 540 390 610 445 675 500 730 555 770 595 |
| Operating Temperature（℃） | 90 |  |  |  |  |
| Ambient Temperature（℃） | 40 | 25 |  |  |  |

Note: ρw— Soil thermal resistivity without moving the moisture out.

ρD— Soil thermal resistivity with moving the moisture out and making soil dried.

The current rating for single core XLPE insulated cable（A）:

Table 22

| Type | YJV YJLV YJY YJLY |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Voltage | 3.6/6-26/35（kV） |  |  |  |  |
| Arrange | Parallel（The distance between two cables is the diameter of the cable） |  |  |  |  |
| Installation | In Air | Underground （k.m/w） |  |  |  |
|  |  | ρw |  | ρD(moving the moisture out) |  |
|  |  | 1.0 | 2.5 | 3.0 | 3.5 |
| Cross-sectional Area（mm2） | Cu. Al. | Cu. Al | Cu. Al | Cu. Al | Cu. Al |
| 50 70 95 120 150 185 240 300 400 500 630 800 1000 1200 | 245 190 305 235 370 285 425 330 485 375 555 430 650 505 745 580 870 680 1000 790 1160 920 1330 1060 1490 1210 1620 1340 | 225 175 275 215 330 255 375 290 420 325 475 370 555 430 630 490 720 565 825 645 940 740 1060 845 1170 950 1280 1030 | 200 155 245 190 295 225 335 260 375 290 420 325 485 380 550 425 630 490 715 560 810 640 910 730 1010 820 1070 890 | 200 155 240 185 290 225 325 255 365 285 410 320 475 370 535 415 615 480 700 550 790 625 890 710 980 800 1050 865 | 195 150 240 185 285 220 320 250 360 280 405 315 470 365 530 400 605 455 685 540 780 615 875 700 960 785 1030 850 |
| Operating Temperature（℃） | 90 |  |  |  |  |
| Ambient Temperature（℃） | 40 | 25 |  |  |  |

Note: ρw— Soil thermal resistivity without moving the moisture out.

ρD— Soil thermal resistivity with moving the moisture out and making soil dried.

The current rating  for three cores XLPE insulated cable（A）:

Table  23

| Type | YJV YJY YJV22 YJV23 YJV32 YJV33 YJV42 YJV43 YJLV YJLY YJLV22 YJLY23 YJLV32 YJLY33 YJLV42 YJLY43 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Voltage | 3.6/6-12/20（kV） |  |  |  |  |  |  |
| Installation | In Air | Underground（k.m/w） |  |  |  |  |  |
|  |  | ρw |  |  | ρD(moving the moisture out) |  |  |
|  |  | 1.0 |  | 2.5 |  | 3.0 | 3.5 |
| Cross-sectional Aera（mm2） | Cu. Al. | Cu. Al. |  | Cu. Al. |  | Cu. Al. | Cu. Al. |
| 25 35 50 70 95 120 150 185 240 300 | 120 90 140 110 165 130 210 165 255 200 390 225 330 255 375 295 435 345 495 390 | 125 100 155 120 180 140 220 170 265 210 300 235 340 260 380 300 435 345 485 390 |  | 120 90 140 110 165 125 205 160 240 185 270 210 300 235 345 265 390 305 435 345 |  | 120 90 140 110 165 125 200 155 235 185 265 210 300 235 335 260 385 305 430 340 | 115 90 135 105 165 125 195 155 235 180 260 205 295 230 330 255 380 300 420 335 |
| Operating Temperature（℃） | 90 |  |  |  |  |  |  |
| Ambient Temperature（℃） | 40 |  | 25 |  |  |  |  |

Note: ρw— Soil thermal resistivity without moving the moisture out.

ρD— Soil thermal resistivity with moving the moisture out and making soil dried.

The current rating  for three cores XLPE insulated cable（A）:

Table 24

| Type | YJV YJY YJV22 YJV23 YJV32 YJV33 YJV42 YJV43 YJLV YJLY YJLV22 YJLY23 YJLV32 YJLY33 YJLV42 YJLY43 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Voltage | 26/35（kV） |  |  |  |  |  |
| Installation | In Air | Underground（k.m/w） |  |  |  |  |
|  |  | ρw |  |  | ρD(moving the moisture out) |  |
|  |  | 1.0 |  | 2.5 | 3.0 | 3.5 |
| Cross-sectional Area（mm2） | Cu. Al. | Cu. Al. |  | Cu. Al. | Cu. Al. | Cu. Al. |
| 50 70 95 120 150 185 240 300 | 180 138 220 174 258 200 285 218 320 252 372 290 437 337 500 378 | 186 140 220 170 263 203 295 230 342 253 370 290 430 340 480 382 |  | 180 136 215 169 242 185 265 205 290 232 315 260 385 297 430 335 | 180 136 210 165 237 185 260 200 290 232 305 255 380 297 425 380 | 180 136 205 165 235 180 255 195 285 227 300 250 275 292 415 325 |
| Operating Temperature（℃） | 90 |  |  |  |  |  |
| Ambient Temperature（℃） | 40 |  | 25 |  |  |  |

Note: ρw— Soil thermal resistivity without moving the moisture out.

ρD— Soil thermal resistivity with moving the moisture out and making soil dried.

The correct factors at different temperature in air:

Table 25

| Conductor Temperature℃ | Ambient Temperature ℃（in air） |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 |
| 90 | 1.26 | 1.22 | 1.18 | 1.14 | 1.09 | 1.04 | 1.00 | 0.94 | 0.89 |

The correct factors in different temperatures underground                    Table 25

| Conductor Temperature℃ | Soil Temperature ℃（in air） |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 10 | 15 | 20 | 25 | 30 | 35 |
| 90 | 1.11 | 1.07 | 1.04 | 1.00 | 0.96 | 0.92 |

The correct factors for current rating  of XLPE cable with different soil coefficient of thermal resistivity.

Table  27

| Rated Voltage kV | Cross-sectional Aera mm2 | Soil Coefficient of thermal Resistivity k.m/w |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | 0.8 | 1.0 | 1.2 | 1.5 | 2.0 |
| 0.6/1-6/6 | <35 50~150 >185 | 1.06 1.08 1.09 | 1.00 1.00 1.00 | 0.92 0.94 0.93 | 0.87 0.85 | 0.77 0.76 |
| 10 | <35 50~120 150~300 >400 | 1.05 1.06 1.07 1.07 | 1.00 1.00 1.00 1.00 | 0.95 0.94 0.94 0.93 | 0.90 0.88 0.87 0.87 | 0.82 0.80 0.78 0.77 |
| 20 and above | 50~95 120~240 ≥300 | 1.05 1.06 1.06 | 1.00 1.00 1.00 | 0.95 0.94 0.93 | 0.90 0.88 0.88 | 0.82 0.80 0.80 |

Note: the correct factors are only suitable for the case of that soil thermal resistivity without moving the moisture out.