TABLE 2   TECHNICAL SPECIFICATION OF

COGENERATION STEAM TURBINES                 2-1

| No. | Designation & code Item Unit |  | 1.5MW Back-pressure turbine | 3MW Single extraction turbine |  | 3MW Single extraction turbine |  | 3MW Extraction Back-pressure turbine |  | 3MW Extraction Back-pressure turbine |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Code |  | 93# | SX03# |  | SX05# |  | SX03# |  | SX07# |  |
| 2 | Model |  | B1.5 .2.35/0.49 | C3 .3.43/0.49 |  | C3 .3.43/0.98 |  | CB3 .3.43/0.98/0.49 |  | CB3 .3.43 /1.57 /0.49 |  |
| 3 | Type |  | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.1-cylinder |  | Impulse tandem- comp.1-cylinder |  | Impulse tandem- comp.1-cylinder |  | Impulse tandem- comp.1-cylinder |  |
| 4 | Rated output | MW | 1.5 | 3 |  | 3 |  | 2.2(extract) |  | 3 |  |
| 5 | Max.output | MW |  |  |  |  |  | 3 |  | 3.3 |  |
| 6 | Speed | r/min | 3000 | 3000 |  | 3000 |  | 3000 |  | 3000 |  |
| 7 | Steam pres.before stop valve | Mpa | 2.35 | 3.43 |  | 3.43 |  | 3.43 |  | 3.43 |  |
| 8 | Steam temp.before stop valve | ℃ | 390 | 435 |  | 435 |  | 435 |  | 435 |  |
| 9 | Rated steam flow | t/h | 22 | 17(condensing) 30(extract) |  | 26 |  | 35 |  | 48 |  |
| 10 | Max steam flow | t/h |  |  |  | 30 |  |  |  |  |  |
| 11 | Extracted steam press. for processing | MPa |  | 0.49 |  | 0.98 |  | 0.98 |  | 1.57 |  |
| 12 | Rated extracted steam flow for processing | t/h |  | 20 |  | 15 |  | 15 |  | 20 |  |
| 13 | Max extracted steam flow for processing | t/h |  |  |  | 19 |  |  |  |  |  |
| 14 | Extracted steam press For district heating | Mpa |  |  |  |  |  |  |  |  |  |
| 15 | Rated extracted steam flow For district heating | T/h |  |  |  |  |  |  |  |  |  |
| 16 | Max extracted steam flow For district heating | T/h |  |  |  |  |  |  |  |  |  |
| 17 | Exhaust press (extract/condens) | MPa | 0.49 | 0.0046/0.0078 |  | 0.0058/0.0077 |  | 0.49 |  | 0.49 |  |
| 18 | No. of stages |  | 1+2 | 1+8 |  | 1+1.1+6 |  | 1+4 |  | 1+1+2 |  |
| 19 | No. of heaters |  |  | 1(HP heater) +1(deaerator) +1(LP heater) |  | 1(HP heater) +1(deaerator) +1(LP heater) |  |  |  |  |  |
| 20 | Cooling of water temp | ℃ |  | 20 |  | 27 |  |  |  |  |  |
| 21 | Feed water temp | ℃ |  | 145 |  | 140 |  |  |  |  |  |
| 22 | Heat rate (extract/condens) | KJ/kW.h |  | 8092/13454 |  | 10507/13845 |  |  |  |  |  |
| 23 | Steam rate (extract/condens) | Kg/kW.h | 14.78 | 10.06/5.54 |  | 8.74/5.09 |  | 16.06(extract) |  | 15.84 |  |
| 24 | Height of last vane | m2 |  | 110 |  | 110 |  |  |  |  |  |
| 25 | Overall size (LxWxH) | m | 2.8x2.3x2.4 | 4.0x2.6x2.3 |  |  |  | 3.9x2.7x1.9 |  | 4.0x2.7x1.9 |  |
| 26 | Turbine wt | t | 16 | 23 |  | 22 |  | 23 |  | 23 |  |
| 27 | Cooling surface of condenser | M2 |  | 250 |  | 250 |  |  |  |  |  |
| Remarks |  |  |  |  |  |  |  |  |  |  |  |