TABLE 2   TECHNICAL SPECIFICATION OF

COGENERATION STEAM TURBINES                2-10

| No. | Designation & code Item Unit |  | 50MW Single extraction turbine | 50MW Back-pressure turbine | 50MW Back-pressure turbine | 50MW Back-pressure turbine | 50MW Double extraction turbine |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Code |  | 68# |  |  | 113# | *52# |
| 2 | Model |  | C50-8.83/0.118 | B50-8.83/0.118 | B50-8.83/0.98 | B50-8.83/1.28 | CC50-8.83/1.57 /0.17 |
| 3 | Type |  | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.2-cylinder |
| 4 | Rated output | MW | 50 | 50 | 50 | 50 | 50 |
| 5 | Max.output | MW | 60 | 55 | 55 | 55 | 60 |
| 6 | Speed | r/min | 3000 | 3000 | 3000 | 3000 | 3600 |
| 7 | Steam pres.before stop valve | Mpa | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 |
| 8 | Steam temp.before stop valve | ℃ | 535 | 535 | 535 | 535 | 535 |
| 9 | Rated steam flow | t/h | 235 | 253 | 398 | 425 | 298 |
| 10 | Max steam flow | t/h | 288 | 280 | 444 | 475 | 360 |
| 11 | Extracted steam press. for processing | MPa |  |  | 0.98 |  | 1.57 |
| 12 | Rated extracted steam flow for processing | t/h |  |  | 339 |  | 113 |
| 13 | Max extracted steam flow for processing | t/h |  |  | 371 |  | 140 |
| 14 | Extracted steam press For district heating | Mpa | 0.118 | 0.118 |  |  | 0.17 |
| 15 | Rated extracted steam flow For district heating | T/h | 160 | 207 |  |  | 60 |
| 16 | Max extracted steam flow For district heating | T/h | 200 | 226 |  |  | 85 |
| 17 | Exhaust press (extract/condens) | MPa | 0.0030/0.0054 | 0.118 | 0.98 | 1.28 | 0.0033/0.055 |
| 18 | No. of stages |  | 1+14+1+3 |  |  | 1+9 | 1+9+1+6+1+3 |
| 19 | No. of heaters |  | 2(HP heater) +1(deaerator) +3(LP heater) | 2(HP heater) +1(deaerator) +1(LP heater) | 1(HP heater) | 2(HP heater) +1(deaerator) | 2(HP heater) +1(deaerator) +3(LP heater) |
| 20 | Cooling of water temp | ℃ | 20 |  |  |  | 20 |
| 21 | Feed water temp | ℃ | 200 | 216 | 225 |  | 217 |
| 22 | Heat rate (extract/condens) | KJ/kW.h | 4928/9510 |  |  |  | 4585/10044 |
| 23 | Steam rate (extract/condens) | Kg/kW.h | 4.71/3.66 | 5.03 | 7.97 |  | 6.01 |
| 24 | Height of last vane | m2 | 665 |  |  |  | 610 |
| 25 | Overall size (LxWxH) | m | 9.5x6.9x3.5 | 8.5x4.6x2.7 | 8.0x4.3x2.7 | 7.51x3.39x3.48 | 12.7x6.9x3.4 |
| 26 | Turbine wt | t | 140 | 80 | 70 | 76 | 180 |
| 27 | Cooling surface of condenser | M2 | 3500 |  |  |  | 3500 |
| Remarks |  | * 60Hz |  |  |  |  |  |