TABLE 2   TECHNICAL SPECIFICATION OF

COGENERATION STEAM TURBINES                2-11

| No. | Designation & code Item Unit |  | 58MW Double extraction turbine | 82MW Single extraction turbine | 100MW Single extraction turbine | 100MW Double ex extraction turbine | 100MW Double extraction turbine |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Code |  | 121# | 43#-4 |  |  |  |
| 2 | Model |  | CC58-8.83/1.27 /0.294 | C82/N100-8.83 /0.196 | C100-8.83/0.98 | CC100-8.83 /1.27/0.196 | CC100-8.83 /4.12/1.47 |
| 3 | Type |  | Impulse tandem- comp.2-cylinder | Impulse tandem- comp.1-cylinder 2-exhaust | Impulse tandem- comp.2-cylinder 2-exhaust | Impulse tandem- comp.2-cylinder 2-exhaust | Impulse tandem- comp.2-cylinder 1-exhaust |
| 4 | Rated output | MW | 58 | 82/100 | 100 | 100 | 100 |
| 5 | Max.output | MW | 60 | 112 | 125 | 125 | 125 |
| 6 | Speed | r/min | 3000 | 3000 | 3000 | 3000 | 3000 |
| 7 | Steam pres.before stop valve | Mpa | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 |
| 8 | Steam temp.before stop valve | ℃ | 535 | 535 | 535 | 535 | 535 |
| 9 | Rated steam flow | t/h | 260.0 | 370 | 444 | 566 | 630 |
| 10 | Max steam flow | t/h | 328 | 417 | 565 | 708 | 700 |
| 11 | Extracted steam press. for processing | MPa | 1.275 |  | 0.98 | 1.27 | 4.12 |
| 12 | Rated extracted steam flow for processing | t/h | 36 |  | 100 | 200 | 160 |
| 13 | Max extracted steam flow for processing | t/h | 60 |  | 135 | 350 | 310 |
| 14 | Extracted steam press For district heating | Mpa | 0.294 | 0.196 |  | 0.196 | 1.47 |
| 15 | Rated extracted steam flow For district heating | T/h | 28 | 150 |  | 150 | 100 |
| 16 | Max extracted steam flow For district heating | T/h | 60 | 220 |  | 250 | 380 |
| 17 | Exhaust press (extract/condens) | MPa | 0.0048/0.0054 | 0.0035/0.0049 | 0.0045/0.0055 | 0.0033/0.0049 | 0.0037/0.050 |
| 18 | No. of stages |  | 1+10+1+6+1+3 | 1+14+2x5 | 1+9+1+3+2x5 | 1+9+1+3+2x5 | 1+3+1+5+1+9 |
| 19 | No. of heaters |  | 2(HP heater) +1(deaerator) +3(LP heater) | 2(HP heater) +1(deaerator) +4(LP heater) | 2(HP heater) +1(deaerator) +4(LP heater) | 2(HP heater) +1(deaerator) +4(LP heater) | 2(HP heater) +1(deaerator) +4(LP heater) |
| 20 | Cooling of water temp | ℃ | 20 | 20 | 20 | 20 | 20 |
| 21 | Feed water temp | ℃ | 218 | 227 | 224 | 223 | 233 |
| 22 | Heat rate (extract/condens) | KJ/kW.h | 8791/9753 | 7080/9253 |  |  | 6827/9231 |
| 23 | Steam rate (extract/condens) | Kg/kW.h | 4.517/3.767 | 4.46/3.96 | 4.42 | 5.66 | 6.30/3.50 |
| 24 | Height of last vane | m2 | 668 | 668 | 668 | 668 | 800 |
| 25 | Overall size (LxWxH) | m | 12.7x7.4x3.4 | 13.8x6.9x4.7 | 13.8x6.9x4.7 | 13.8x6.9x4.7 | 12.5x7.8x5.4 |
| 26 | Turbine wt | t |  | 270 | 270 | 270 | 240 |
| 27 | Cooling surface of condenser | M2 | 3500 | 7000 | 7000 | 7000 | 7000 |
| Remarks |  |  |  |  |  |  |  |