TABLE 2   TECHNICAL SPECIFICATION OF

COGENERATION STEAM TURBINES               2-12

| No. | Designation & code Item Unit |  | *60MW Double extraction turbine | **60MW Single extraction turbine |  | ***60MW Single extraction turbine |  | ****80MW Double Extraction turbine |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Code |  | G37# | G38# |  | Sx27# |  |  |  |  |
| 2 | Model |  | CC60-8.83/4.12 /1.47 | C60. 8.83/1.27 |  | C60-8.83/1.27 |  | C80/N100-8.83 /0.98/0.196 |  |  |
| 3 | Type |  | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.1-cylinder |  | Impulse tandem- comp.1-cylinder |  | Impulse tandem- comp.2-cylinder |  |  |
| 4 | Rated output | MW | 60 | 60 |  | 60 |  | 80/100 |  |  |
| 5 | Max.output | MW | 63 | 63 |  | 63 |  | 113 |  |  |
| 6 | Speed | r/min | 3000 | 3000 |  | 3000 |  | 3000 |  |  |
| 7 | Steam pres.before stop valve | Mpa | 8.83 | 8.83 |  | 8.83 |  | 8.83 |  |  |
| 8 | Steam temp.before stop valve | ℃ | 535 | 535 |  | 535 |  | 535 |  |  |
| 9 | Rated steam flow | t/h | 408 | 372 |  | 382 |  | 379 |  |  |
| 10 | Max steam flow | t/h | 420 | 410 |  | 420 |  | 417 |  |  |
| 11 | Extracted steam press. for processing | MPa | 4.12 | 1.27 |  | 1.27 |  | 0.981 |  |  |
| 12 | Rated extracted steam flow for processing | t/h | 75 | 200 |  | 200 |  | 60 |  |  |
| 13 | Max extracted steam flow for processing | t/h | 180 | 230 |  | 230 |  | 100 |  |  |
| 14 | Extracted steam press For district heating | Mpa | 1.47 |  |  |  |  | 0.196 |  |  |
| 15 | Rated extracted steam flow For district heating | T/h | 120 |  |  |  |  |  | 120 |  |
| 16 | Max extracted steam flow For district heating | T/h | 210 |  |  |  |  |  | 200 |  |
| 17 | Exhaust press (extract/condens) | MPa | 0.0031/0.0059 | 0.0031/0.0053 |  | 0.0038/0.0050 |  | 0.0038/0.0050 |  |  |
| 18 | No. of stages |  | 1+2+1+3+1+8 | 1+6+1+9 |  | 1+7+1+10 |  | 1+9+1+4+2x5 |  |  |
| 19 | No. of heaters |  | 2(HP heater) +1(deaerator) +3(LP heater) | 2(HP heater) +1(deaerator) +3(LP heater) |  | 2(HP heater) +1(deaerator) +3(LP heater) |  | 2(HP heater) +1(deaerator) +4(LP heater) |  |  |
| 20 | Cooling of water temp | ℃ | 20 | 20 |  | 20 |  | 20 |  |  |
| 21 | Feed water temp | ℃ | 220 | 220 |  | 215 |  | 226 |  |  |
| 22 | Heat rate (extract/condens) | KJ/kW.h | 6685/10017 | 5870/9860 |  | 6310/9670 |  | 6528/9023 |  |  |
| 23 | Steam rate (extract/condens) | Kg/kW.h | 6.817/3.896 | 7.084/3.770 |  | 6.44/3.65 |  | 4.741/3.603 |  |  |
| 24 | Height of last vane | m2 | 540 | 540 |  | 668 |  | 668 |  |  |
| 25 | Overall size (LxWxH) | m | 8.4x4.43x3.5 | 8.0x5.0x3.5 |  | 9.5x6.9x3.5 |  |  |  |  |
| 26 | Turbine wt | t | 125 | 192 |  | 145 |  |  |  |  |
| 27 | Cooling surface of condenser | M2 | 3500 | 3500 |  | 3500 |  |  |  |  |
| Remarks |  | *The alteration from old 50000 double extraction turbine to expand capacity ** The alteration from old 50000 single extraction turbine to expand capacity *** The alteration from old 50000 single extraction turbine (63#) to expand capacity **** The alteration from old 100000 condensing turbine (43#) to be changed to double exhaust turbine. |  |  |  |  |  |  |  |  |