TABLE 2   TECHNICAL SPECIFICATION OF

COGENERATION STEAM TURBINES                 2-3

| No. | Designation & code Item Unit |  | 6MW Back-pressure turbine | 12MW Double extraction turbine |  | 12MW Double extraction turbine |  | 12MW Double extraction turbine |  | 12MW Back-pressure turbine |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Code |  |  | 101# |  | 104# |  | 107# |  | 77# |
| 2 | Model |  | B6. 3.43/0.49 | CC12-3.43/0.98 /0.118 |  | CC12-4.9/0.98 /0.245 |  | CC12-3.43/1.47 /0.294 |  | B12-8.83/4.022 |
| 3 | Type |  | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.1-cylinder |  | Impulse tandem- comp.1-cylinder |  | Impulse tandem- comp.2-cylinder |  | Impulse tandem- comp.1-cylinder |
| 4 | Rated output | MW | 6 | 12 |  | 12 |  | 12 |  | 12 |
| 5 | Max.output | MW |  | 14 |  | 15 |  | 14 |  | 14 |
| 6 | Speed | r/min | 3000 | 3000 |  | 3000 |  | 3000 |  | 3000 |
| 7 | Steam pres.before stop valve | Mpa | 3.43 | 3.43 |  | 4.9 |  | 3.43 |  | 8.83 |
| 8 | Steam temp.before stop valve | ℃ | 435 | 435 |  | 435 |  | 435 |  | 535 |
| 9 | Rated steam flow | t/h | 65 | 114 |  | 95 |  | 130 |  | 254 |
| 10 | Max steam flow | t/h |  | 130 |  | 110 |  | 150 |  | 280 |
| 11 | Extracted steam press. for processing | MPa |  | 0.98 |  | 0.98 |  | 1.47 |  |  |
| 12 | Rated extracted steam flow for processing | t/h |  | 50 |  | 30 |  | 50 |  |  |
| 13 | Max extracted steam flow for processing | t/h |  | 80 |  | 65 |  | 70 |  |  |
| 14 | Extracted steam press For district heating | Mpa |  | 0.118 |  | 0.245 |  | 0.294 |  |  |
| 15 | Rated extracted steam flow For district heating | T/h |  |  | 40 |  | 40 | 40 |  |  |
| 16 | Max extracted steam flow For district heating | T/h |  |  | 60 |  | 70 | 70 |  |  |
| 17 | Exhaust press (extract/condens) | MPa | 0.49 | 0.004/0.0008 |  | 0.0035/0.007 |  | 0.0034/0.0073 |  | 4.02 |
| 18 | No. of stages |  | 1+4 | 11+1+1+3+1+3 |  | 11+3+1+3+1+4 |  | 1+1+1+3+1+4 |  | 1+3 |
| 19 | No. of heaters |  |  | 3(HP heater) +1(deaerator) +1(LP heater) |  | 1(HP heater) +1(deaerator) +1(LP heater) |  | 2(HP heater) +1(deaerator) +1(LP heater) |  |  |
| 20 | Cooling of water temp | ℃ |  | 20 |  | 20 |  | 20 |  |  |
| 21 | Feed water temp | ℃ |  | 170 |  | 150 |  | 189 |  |  |
| 22 | Heat rate (extract/condens) | KJ/kW.h |  | 4460/12617 |  | 6152/11815 |  | 7093/12856 |  |  |
| 23 | Steam rate (extract/condens) | Kg/kW.h |  | 9.45/4.7 |  | 7.95/4.46 |  | 10.7/4.8 |  | 21.12 |
| 24 | Height of last vane | m2 |  | 260 |  | 260 |  | 260 |  | 31 |
| 25 | Overall size (LxWxH) | m | 4.0x2.6x2.3 | 6.25x3.53x3.56 |  | 6.9x3.5x2.5 |  | 4.7x3.6x4.2 |  | 6.8x3.3x3.4 |
| 26 | Turbine wt | t | 23 | 56.5 |  | 87 |  | 68 |  | 62 |
| 27 | Cooling surface of condenser | M2 |  | 1000 |  | 900 |  | 700 |  |  |
| Remarks |  |  |  |  |  |  |  |  |  |  |