TABLE 2   TECHNICAL SPECIFICATION OF

COGENERATION STEAM TURBINES                       2-4

| No. | Designation & code Item Unit |  | 12MW Back-pressure turbine | 12MW Back-pressure turbine | 12MW Back-pressure turbine |  | 25MW Back-pressure turbine |  | 25MW Single extraction turbine | 25MW Double extraction turbine |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Code |  | 128# |  | 103# |  | 122# |  |  | 119# |
| 2 | Model |  | B12. 8.83/3.04 | B12. 4.90/0.981 | B12. 4.90/0.686 |  | B25. 8.83/0.981 |  | C25. 3.43/0.98 | CC25. 3.43/0.98/0.196 |
| 3 | Type |  | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.1-cylinder |  | Impulse tandem- comp.1-cylinder |  | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.1-cylinder |
| 4 | Rated output | MW | 12 | 12 | 12 |  | 25 |  | 25 | 25 |
| 5 | Max.output | MW | 13.5 | 14 | 13 |  | 30 |  | 30 | 30 |
| 6 | Speed | r/min | 3000 | 3000 | 3000 |  | 3000 |  | 3000 | 3000 |
| 7 | Steam pres.before stop valve | Mpa | 8.83 | 4.90 | 4.90 |  | 8.83 |  | 3.43 | 3.43 |
| 8 | Steam temp.before stop valve | ℃ | 535 | 435 | 435 |  | 535 |  | 435 | 435 |
| 9 | Rated steam flow | t/h | 200 | 148 | 123 |  | 200 |  | 161 | 195 |
| 10 | Max steam flow | t/h | 230 | 170 | 132 |  | 260 |  | 193 | 215 |
| 11 | Extracted steam press. for processing | MPa |  |  |  |  |  |  | 0.98 | 0.98 |
| 12 | Rated extracted steam flow for processing | t/h |  |  |  |  |  |  | 60 | 60 |
| 13 | Max extracted steam flow for processing | t/h |  |  |  |  |  |  | 100 | 100 |
| 14 | Extracted steam press For district heating | Mpa |  |  |  |  |  |  |  | 0.196 |
| 15 | Rated extracted steam flow For district heating | T/h |  |  |  |  |  |  |  | 60 |
| 16 | Max extracted steam flow For district heating | T/h |  |  |  |  |  |  |  | 100 |
| 17 | Exhaust press (extract/condens) | MPa | 3.04 | 0.981 | 0.686 |  | 0.981 |  | 0.0034/0.0049 | 0.0034/0.0049 |
| 18 | No. of stages |  | 1+4 | 11+3 | 1+5 |  | 1+10 |  | 1+2+1+8 | 1+1+1+4+1+3 |
| 19 | No. of heaters |  |  | 1(HP heater) +1(deaerator) +1(LP heater) |  |  | 2(HP heater) |  | 2(HP heater) +1(deaerator) +1(LP heater) | 2(HP heater) +1(deaerator) +1(LP heater) |
| 20 | Cooling of water temp | ℃ |  |  |  |  |  |  | 20 | 20 |
| 21 | Feed water temp | ℃ |  | 150.4 |  |  | 220 |  | 170 | 170 |
| 22 | Heat rate (extract/condens) | KJ/kW.h |  | 3863 |  |  |  |  | 10068/11698 | 7658/12008 |
| 23 | Steam rate (extract/condens) | Kg/kW.h | 17.1 | 12.31 | 10.25 |  | 8.0 |  | 6.44/4.46 | 7.74/4.64 |
| 24 | Height of last vane | m2 |  |  |  |  |  |  | 432 | 432 |
| 25 | Overall size (LxWxH) | m | 4.0x2.6x2.3 | 4.0x2.6x2.3 | 4.9x3.5x2.3 |  | 6.2x4.1x2.5 |  | 7.2x4.4x2.7 | 7.2x4.4x2.7 |
| 26 | Turbine wt | t | 23 | 23 | 34 |  | 70 |  | 100 | 100 |
| 27 | Cooling surface of condenser | M2 |  |  |  |  |  |  | 2000 | 2000 |
| Remarks |  |  |  |  |  |  |  |  |  |  |