TABLE 2   TECHNICAL SPECIFICATION OF

COGENERATION STEAM TURBINES                 2-5

| No. | Designation & code Item Unit |  | 25MW Single extraction turbine | 25MW Single extraction turbine |  | 25MW Single extraction turbine |  | 25MW Single extraction turbine |  | 25MW Double extraction turbine |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Code |  | 115# |  |  | 117# |  |  |  | 65# |
| 2 | Model |  | C25. 8.83/1.275 | C25. 11.28/4.41 |  | C25. 8.83/0.98 |  | C25. 8.83/0.118 |  | CC25. 8.83/0.98/0.118 |
| 3 | Type |  | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.1-cylinder |  | Impulse tandem- comp.1-cylinder |  | Impulse tandem- comp.1-cylinder |  | Impulse tandem- comp.1-cylinder |
| 4 | Rated output | MW | 25 | 25 |  | 25 |  | 25 |  | 25 |
| 5 | Max.output | MW | 30 | 30 |  | 30 |  | 30 |  | 30 |
| 6 | Speed | r/min | 3000 | 3000 |  | 3000 |  | 3000 |  | 3000 |
| 7 | Steam pres.before stop valve | Mpa | 8.83 | 11.28 |  | 8.83 |  | 8.83 |  | 8.83 |
| 8 | Steam temp.before stop valve | ℃ | 535 | 535 |  | 535 |  | 535 |  | 535 |
| 9 | Rated steam flow | t/h | 128 | 200 |  | 169 |  | 125 |  | 153 |
| 10 | Max steam flow | t/h | 200 | 220 |  | 211 |  | 168 |  | 210 |
| 11 | Extracted steam press. for processing | MPa | 1.275 | 4.41 |  | 0.98 |  |  |  | 0.98 |
| 12 | Rated extracted steam flow for processing | t/h | 40 | 110 |  | 110 |  |  |  | 60 |
| 13 | Max extracted steam flow for processing | t/h | 100 | 130 |  | 130 |  |  |  | 100 |
| 14 | Extracted steam press For district heating | Mpa |  |  |  |  |  | 0.118 |  | 0.118 |
| 15 | Rated extracted steam flow For district heating | T/h |  |  |  |  |  | 85 | 46 |  |
| 16 | Max extracted steam flow For district heating | T/h |  |  |  |  |  | 115 | 90 |  |
| 17 | Exhaust press (extract/condens) | MPa | 0.0046/0.0061 | 0.0050/0.0060 |  | 0.0073/0.0053 |  | 0.0034/0.0053 |  | 0.0028/0.0048 |
| 18 | No. of stages |  | 1+10+1+9 | 11+1+1+17 |  | 1+11+1+9 |  | 1+17+1+3 |  | 1+10+1+4+1+3 |
| 19 | No. of heaters |  | 2(HP heater) +1(deaerator) +3(LP heater) | 2(HP heater) +1(deaerator) +3(LP heater) |  | 2(HP heater) +1(deaerator) +3(LP heater) |  | 2(HP heater) +1(deaerator) +3(LP heater) |  | 4(HP heater) +2(deaerator) +1(LP heater) |
| 20 | Cooling of water temp | ℃ | 20 | 20 |  | 20 |  | 20 |  | 20 |
| 21 | Feed water temp | ℃ | 210 | 226 |  | 218 |  | 212 |  | 213 |
| 22 | Heat rate (extract/condens) | KJ/kW.h | 8951/10301 | 7975/10075 |  | 5870/9948 |  | 5404/9973 |  | 5324/10248 |
| 23 | Steam rate (extract/condens) | Kg/kW.h | 5.129/3.926 | 7.985/4.070 |  | 6.77/3.81 |  | 4.99/3.86 |  | 6.11/3.88 |
| 24 | Height of last vane | m2 | 432 | 432 |  | 432 |  | 432 |  | 432 |
| 25 | Overall size (LxWxH) | m | 9.1x4.4x2.7 | 12.16x4.48x3.38 |  | 9.1x4.4x2.7 |  | 9.1x4.4x2.7 |  | 9.1x4.4x2.7 |
| 26 | Turbine wt | t | 120 | 157.4 |  | 120 |  | 122 |  | 120 |
| 27 | Cooling surface of condenser | M2 | 2000 | 2000 |  | 2000 |  | 2000 |  | 2000 |
| Remarks |  |  |  |  |  |  |  |  |  |  |