TABLE 2   TECHNICAL SPECIFICATION OF

COGENERATION STEAM TURBINES                 2-6

| No. | Designation & code Item Unit |  | 25MW Double extraction turbine | 25MW Double extraction turbine | 25MW Double extraction turbine |  | 25MW Double extraction turbine |  | 25MW Extraction & Back-pressure turbine |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Code |  | 65#-2 | 76# | 76#-1 |  | 79# |  | 66# |  |
| 2 | Model |  | CC25-8.83/1.28 /0.118 | CC25-8.83/4.02 /0.98 | CC25-8.83/4.02 /0.98 |  | CC25-8.83/4.02 /1.28 |  | CB25. 8.83/0.98/0.118 |  |
| 3 | Type |  | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.1-cylinder |  | Impulse tandem- comp.2-cylinder |  | Impulse tandem- comp.1-cylinder |  |
| 4 | Rated output | MW | 25 | 25 | 25 |  | 25 |  | 25 |  |
| 5 | Max.output | MW | 30 | 30 | 30 |  | 30 |  | 30 |  |
| 6 | Speed | r/min | 3000 | 3000 | 3000 |  | 3000 |  | 3000 |  |
| 7 | Steam pres.before stop valve | Mpa | 8.83 | 8.83 | 8.83 |  | 8.83 |  | 8.83 |  |
| 8 | Steam temp.before stop valve | ℃ | 535 | 535 | 535 |  | 535 |  | 535 |  |
| 9 | Rated steam flow | t/h | 155 | 256 | 198.6 |  | 231 |  | 156 |  |
| 10 | Max steam flow | t/h | 197 | 280 | 220 |  | 272 |  | 210 |  |
| 11 | Extracted steam press. for processing | MPa | 1.28 | 4.02 | 4.02 |  | 4.02 |  | 0.98 |  |
| 12 | Rated extracted steam flow for processing | t/h | 60 | 120 | 60 |  | 60 |  | 60 |  |
| 13 | Max extracted steam flow for processing | t/h | 100 | 140 | 140 |  | 80 |  | 120 |  |
| 14 | Extracted steam press For district heating | Mpa | 0.118 | 0.98 | 0.98 |  | 1.28 |  |  |  |
| 15 | Rated extracted steam flow For district heating | T/h | 40 | 60 | 60 | 100 |  |  |  |  |
| 16 | Max extracted steam flow For district heating | T/h | 90 | 70 | 140 | 130 |  |  |  |  |
| 17 | Exhaust press (extract/condens) | MPa | 0.0029/0.0047 | 0.007/0.0102 | 0.0047/0.0062 |  | 0.0031/0.0048 |  | 0.118 |  |
| 18 | No. of stages |  | 1+10+1+5+1+3 | 1+3+1+5+1+9 | 1+3+1+5+1+9 |  | 1+3+1+4+1+9 |  | 1+10+1+4 |  |
| 19 | No. of heaters |  | 2(HP heater) +1(deaerator) +3(LP heater) | 3(HP heater) +1(deaerator) +2(LP heater) | 2(HP heater) +1(deaerator) +2(LP heater) |  | 2(HP heater) +1(deaerator) +2(LP heater) |  | 1(HP heater) +1(deaerator) +1(LP heater) |  |
| 20 | Cooling of water temp | ℃ | 20 | 20 | 20 |  | 20 |  | 20 |  |
| 21 | Feed water temp | ℃ | 217 | 214 | 206 |  | 215 |  | 213 |  |
| 22 | Heat rate (extract/condens) | KJ/kW.h | 5907/10272 | 6473/10709 | 7541/10472 |  | 6348/10449 |  | 3997 |  |
| 23 | Steam rate (extract/condens) | Kg/kW.h | 6.2/3.91 | 10.26/4.13 | 7.94/3.96 |  | 9.24/3.94 |  | 5.5 |  |
| 24 | Height of last vane | m2 | 432 | 432 | 432 |  | 432 |  | 100 |  |
| 25 | Overall size (LxWxH) | m | 8.9x4.4x3.3 | 12.2x4.3x3.4 | 12.2x4.3x3.4 |  | 12.2x4.3x3.4 |  | 8.9x4.4x2.7 |  |
| 26 | Turbine wt | t | 122 | 146 | 146 |  | 146 |  | 90 |  |
| 27 | Cooling surface of condenser | M2 | 2000 | 2000 | 2000 |  | 2000 |  |  |  |
| Remarks |  |  |  |  |  |  |  |  |  |  |