TABLE 2   TECHNICAL SPECIFICATION OF

COGENERATION STEAM TURBINES                       2-7

| No. | Designation & code Item Unit |  | 25MW Back-pressure turbine | 25MW Back-pressure turbine | 25MW Double extraction turbine |  | 25MW Single extraction turbine |  | 25MW Double extraction turbine | 25MW Double extraction turbine |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Code |  |  |  | 114# |  | Sx21# |  | 129# | 130# |
| 2 | Model |  | B25-8.83/0.118 | B25-8.83/1.28 | CC25-10/4.02/0.7 |  | C25-3.43/0.49 |  | CC25-8.83/0.981 /0.29 | CC25-8.9/0.981 /0.118 |
| 3 | Type |  | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.2-cylinder |  | Impulse tandem- comp.1-cylinder |  | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.1-cylinder |
| 4 | Rated output | MW | 25 | 25 | 25 |  | 25 |  | 25 | 25 |
| 5 | Max.output | MW |  |  | 30 |  | 30 |  | 30 | 30 |
| 6 | Speed | r/min | 3000 | 3000 | 3000 |  | 3000 |  | 3000 | 3000 |
| 7 | Steam pres.before stop valve | Mpa | 8.83 | 8.83 | 10 |  | 3.43 |  | 8.83 | 8.90 |
| 8 | Steam temp.before stop valve | ℃ | 535 | 535 | 535 |  | 435 |  | 535 | 535 |
| 9 | Rated steam flow | t/h | 130 | 225 | 197 |  | 166.8 |  | 175 | 155 |
| 10 | Max steam flow | t/h | 145 | 260 | 220 |  | 191 |  | 210 | 210 |
| 11 | Extracted steam press. for processing | MPa |  | 1.28 | 4.02 |  |  |  | 0.981 | 0.981 |
| 12 | Rated extracted steam flow for processing | t/h |  | 195 | 65 |  |  |  | 65 | 72 |
| 13 | Max extracted steam flow for processing | t/h |  |  | 75 |  |  |  | 110 | 130 |
| 14 | Extracted steam press For district heating | Mpa | 0.118 |  | 0.7 |  | 0.49 |  | 0.294 | 0.118 |
| 15 | Rated extracted steam flow For district heating | T/h | 106 |  | 65 | 85 |  | 50 |  | 40 |
| 16 | Max extracted steam flow For district heating | T/h |  |  | 80 |  |  | 90 |  | 90 |
| 17 | Exhaust press (extract/condens) | MPa | 0.118 | 1.28 | 0.0035/0.0053 |  | 0.0057 |  | 0.0028/0.0049 | 0.0038/0.0051 |
| 18 | No. of stages |  | 1+17 | 1+10 | 1+3+1+5+1+8 |  | 1+3+1+6 |  | 1+10+1+4+1+3 | 1+9+1+5+1+3 |
| 19 | No. of heaters |  | 2(HP heater) +1(deaerator) +1(LP heater) | 1(HP heater) | 2(HP heater) +1(deaerator) +2(LP heater) |  | 1(HP heater) +1(deaerator) +1(LP heater) |  | 2(HP heater) +1(deaerator) | 2(HP heater) +1(deaerator) +3(LP heater) |
| 20 | Cooling of water temp | ℃ |  |  | 22 |  | 26 |  | 20 | 20 |
| 21 | Feed water temp | ℃ | 223 | 225 | 204 |  | 170 |  | 217 | 214 |
| 22 | Heat rate (extract/condens) | KJ/kW.h |  |  | 6485/10329 |  | 8728/12062 |  | 5460/10519 | 4972/10153 |
| 23 | Steam rate (extract/condens) | Kg/kW.h | 5.2 | 9.0 | 7.86/3.93 |  | 6.512/4.530 |  |  | 5.91/3.69 |
| 24 | Height of last vane | m2 |  |  | 432 |  | 432 |  | 432 | 433 |
| 25 | Overall size (LxWxH) | m | 8.4x4.0x2.7 | 7.3x4.34x2.7 | 12.16x4.88x3.38 |  | 7.12x4.34x3.56 |  | 8.9x4.4x3.3 | 8.9x4.4x3.3 |
| 26 | Turbine wt | t | 65 | 60 | 157.4 |  | 103 |  | 157.4 | 158 |
| 27 | Cooling surface of condenser | M2 |  |  | 2000 |  | 2000 |  | 2000 | 2000 |
| Remarks |  |  |  |  |  |  |  |  |  |  |