TABLE 2   TECHNICAL SPECIFICATION OF

COGENERATION STEAM TURBINES                 2-8

| No. | Designation & code Item Unit |  | 50MW Double extraction turbine | 50MW Double extraction turbine | 50MW Double extraction turbine | 50MW Single extraction turbine | 50MW Single extraction turbine |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Code |  | 112# | 112-1# | 112-2# | 125# | 102# |
| 2 | Model |  | CC50-8.83/4.02 /1.27 | CC50-8.83/4.22 /1.57 | CC50-8.83/4.12 /1.275 | N50/C40-8.83 /0.98 | C50-8.83/0.98 |
| 3 | Type |  | Impulse tandem- comp.2-cylinder | Impulse tandem- comp.2-cylinder | Impulse tandem- comp.2-cylinder | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.1-cylinder |
| 4 | Rated output | MW | 50 | 50 | 50 | 50 | 50 |
| 5 | Max.output | MW | 60 | 60 | 60 | 60 | 60 |
| 6 | Speed | r/min | 3000 | 3000 | 3000 | 3000 | 3000 |
| 7 | Steam pres.before stop valve | Mpa | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 |
| 8 | Steam temp.before stop valve | ℃ | 535 | 535 | 535 | 535 | 535 |
| 9 | Rated steam flow | t/h | 394 | 354 | 322 | 210 | 330 |
| 10 | Max steam flow | t/h | 410 | 420 | 381 | 220 | 390 |
| 11 | Extracted steam press. for processing | MPa | 4.02 | 4.22 | 4.12 | 0.981 | 0.981 |
| 12 | Rated extracted steam flow for processing | t/h | 50 | 75 | 90 | 90 | 200 |
| 13 | Max extracted steam flow for processing | t/h | 70 | 100 | 120 | 120 | 230 |
| 14 | Extracted steam press For district heating | Mpa | 1.27 | 1.57 | 1.275 |  |  |
| 15 | Rated extracted steam flow For district heating | T/h | 220 | 120 | 80 |  |  |
| 16 | Max extracted steam flow For district heating | T/h | 240 | 180 | 120 |  |  |
| 17 | Exhaust press (extract/condens) | MPa | 0.0031/0.0053 | 0.0031/0.0053 | 0.0038/0.0052 | 0.0038/0.0052 | 0.0039/0.0055 |
| 18 | No. of stages |  | 1+4+1+5+1+9 | 1+4+1+5+1+9 | 1+4+1+5+1+9 | 1+9+1+8 | 1+7+1+9 |
| 19 | No. of heaters |  | 2(HP heater) +1(deaerator) +3(LP heater) | 2(HP heater) +1(deaerator) +3(LP heater) | 2(HP heater) +1(deaerator) +3(LP heater) | 2(HP heater) +1(deaerator) +4(LP heater) | 2(HP heater) +1(deaerator) +3(LP heater) |
| 20 | Cooling of water temp | ℃ | 20 | 20 | 20 | 20 | 20 |
| 21 | Feed water temp | ℃ | 212 | 210 | 197 | 225 | 215 |
| 22 | Heat rate (extract/condens) | KJ/kW.h | 5295/9855 | 7533/9869 | 7511/9655 | 6739/9155 | 5250/9860 |
| 23 | Steam rate (extract/condens) | Kg/kW.h | 7.877/3.78 | 7.084/3.770 | 6.44/3.65 | 5.35/3.60 | 6.57/3.82 |
| 24 | Height of last vane | m2 | 520 | 668 | 668 | 668 | 665 |
| 25 | Overall size (LxWxH) | m | 13.1x7.43x3.48 | 13.1x7.43x3.48 | 13.1x7.43x3.48 | 9.5x6.9x3.5 | 9.5x6.9x3.5 |
| 26 | Turbine wt | t | 192 | 192 | 192 | 140 | 140 |
| 27 | Cooling surface of condenser | M2 | 3500 | 3500 | 3500 | 3500 | 3500 |
| Remarks |  |  |  |  |  |  |  |