TABLE 2   TECHNICAL SPECIFICATION OF

COGENERATION STEAM TURBINES                 2-9

| No. | Designation & code Item Unit |  | 50MW Double extraction turbine | 50MW Double extraction turbine | 50MW Double extraction turbine | 50MW Single extraction turbine | 50MW Single extraction turbine |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Code |  | 62#-1 | 62#-5 | 131# | 63# | 63#-5 |
| 2 | Model |  |  |  |  |  |  |
| 3 | Type |  | Impulse tandem- comp.2-cylinder | Impulse tandem- comp.2-cylinder | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.1-cylinder | Impulse tandem- comp.1-cylinder |
| 4 | Rated output | MW | 50 | 50 | 50 | 50 | 50 |
| 5 | Max.output | MW | 60 | 60 | 60 | 60 | 55 |
| 6 | Speed | r/min | 3000 | 3000 | 3000 | 3000 | 3000 |
| 7 | Steam pres.before stop valve | Mpa | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 |
| 8 | Steam temp.before stop valve | ℃ | 535 | 535 | 535 | 535 | 535 |
| 9 | Rated steam flow | t/h | 322 | 299 | 314 | 341 | 284 |
| 10 | Max steam flow | t/h | 338 | 358 | 370 | 396.8 | 350 |
| 11 | Extracted steam press. for processing | MPa | 1.28 | 0.98 | 0.98 | 1.27 | 1.57 |
| 12 | Rated extracted steam flow for processing | t/h | 120 | 120 | 120 | 200 | 120 |
| 13 | Max extracted steam flow for processing | t/h | 230 | 200 | 210 | 230 | 180 |
| 14 | Extracted steam press For district heating | Mpa | 0.118 | 0.118 | 0.147 |  |  |
| 15 | Rated extracted steam flow For district heating | T/h | 80 | 90 | 70 |  |  |
| 16 | Max extracted steam flow For district heating | T/h | 160 | 150 | 160 |  |  |
| 17 | Exhaust press (extract/condens) | MPa | 0.0027/0.0049 | 0.0030/0.0054 | 0.0030/0.0054 | 0.0039/0.0054 | 0.0042/0.0053 |
| 18 | No. of stages |  | 1+10+1+7+1+3 | 1+10+1+6+1+3 | 1+8+1+4+1+3 | 1+7+1+10 | 1+7+1+9 |
| 19 | No. of heaters |  | 2(HP heater) +1(deaerator) +3(LP heater) | 2(HP heater) +1(deaerator) +3(LP heater) | 2(HP heater) +1(deaerator) +3(LP heater) | 2(HP heater) +1(deaerator) +3(LP heater) | 2(HP heater) +1(deaerator) +3(LP heater) |
| 20 | Cooling of water temp | ℃ | 20 | 20 | 20 | 20 | 20 |
| 21 | Feed water temp | ℃ | 221 | 221 | 216 | 223 | 22 |
| 22 | Heat rate (extract/condens) | KJ/kW.h | 4601/9960 | 4844/9927 | 4480/9670 | 5502/10092 | 7548/9593 |
| 23 | Steam rate (extract/condens) | Kg/kW.h | 6.44/3.83 | 5.98/3.86 | 6.44/3.82 | 6.81/3.86 | 5.17/3.65 |
| 24 | Height of last vane | m2 | 665 | 668 | 668 | 665 | 668 |
| 25 | Overall size (LxWxH) | m | 12.7x7.4x3.4 | 12.5x6.9x2.7 | 9.5x6.9x3.5 | 9.5x6.9x3.5 | 9.5x6.9x3.5 |
| 26 | Turbine wt | t | 184 | 185 | 135 | 135 | 135 |
| 27 | Cooling surface of condenser | M2 | 3500 | 3500 | 3500 | 3500 | 3500 |
| Remarks |  |  |  |  |  |  |  |