TABLE 3   TECHNICAL SPECIFICATION OF

JOINTED CYCLE STEAM TURBINES                         3-2

| No. | Designation & code Item Unit |  | *25MW Condensing turbine | *50MW Condensing turbine | **117MW Condensing turbine | **121MW Condensing turbine | ***190MW Condensing turbine |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Code |  |  | 127# |  |  |  |
| 2 | Model |  | N50-9.7/510 | N50-9.7/510 | N17-11.3/3.10 /0.45 550/550/233 | N121-4.56/500 | N190-7.85/2.06 /0.44 515/287/217 |
| 3 | Type |  | Impulse 1-cylinder axes way -exhaust | Impulse 1-cylinder axes way -exhaust | Impulse 3-press reheat & 2-cylinder 1-exhaust | Impulse 2-press 2-cylinder 2-exhaust | Impulse 3-press 2-cylinder 2-exhaust |
| 4 | Rated output | MW | 25 | 50 | 117.0 | 121 | 187.50 |
| 5 | Max.output | MW | 27 | 53 | >120 | 130 | 200 |
| 6 | Speed | r/min | 3000 | 3000 | 3000 | 3000 | 3000 |
| 7 | Steam pres.before stop valve | Mpa | 9.7 | 9.7 | 11.30 | 4.56 | 7.845 |
| 8 | Steam temp.before stop valve | ℃ | 510 | 510 | 550 | 500 | 540 |
| 9 | Rated steam flow | t/h | 87 | 170 | 253.0 | 370 | 540 |
| 10 | Max steam flow | t/h | 92 | 180 | 270.0 | 390 | 300 |
| 11 | The second steam press. | MPa |  |  | 3.10 | 0.266 | 2.06 |
| 12 | The second steam temp. | ℃ |  |  | 550 (reheat) | 140 | 287 |
| 13 | The rated second steam flow | t/h |  |  | 49.0 | 92 | 78.90 |
| 14 | The max second steam flow | t/h |  |  | 54.0 | 98 | 82 |
| 15 | The third steam press. | MPa |  |  | 0.45 |  | 0.441 |
| 16 | The third steam temp. | ℃ |  |  | 233 |  | 217 |
| 17 | The rated third steam flow | t/h |  |  | 33.0 |  | 46.0 |
| 18 | The max third steam flow | t/h |  |  | 36.0 |  | 48.0 |
| 19 | Exhaust press | MPa | 0.0087 | 0.0088 | 6.90 | 0.0065 | 10.0 |
| 20 | No. of stages |  | 16 | 16 | 12+6+6 | 12+2x5 | 13+2x5 |
| 21 | No. of heaters |  |  |  |  |  |  |
| 22 | Cooling of water temp | ℃ | 30 | 30 | 25 | 25 | 32 |
| 23 | Feed water temp | ℃ | 45 | 45 |  | 42 |  |
| 24 | Heat rate | KJ/kW.h | 11095 | 10978 | 10213 | 12018 |  |
| 25 | Steam rate | Kg/kW.h | 3.49 | 3.43 | 2.855 | 3.818 |  |
| 26 | Height of last vane | m2 | 432 | 520 | 855 | 710 | 900 |
| 27 | Overall size (LxWxH) | m | 8.0x6.5x2.6 | 8.6x6.9x2.6 | 13.5x7.4x5.4 | 13.5x7.0x4.9 |  |
| 28 | Turbine wt | t | 102 | 120 | 320 | 220 |  |
| 29 | Cooling surface of condenser | M2 | 2800 | 5500 | 10000 | 11000 |  |
|  |  |  |  |  | Natural gas | Natural gas | Natural gas |
| Remarks: |  | *Used in Ship substations or fixed substation, axes way exhaust; **To choose 9E type burning machine, two driving one *** To choose 9E type burning machine, three driving one |  |  |  |  |  |