Weatherability Insulated Aerial Cable

Weatherability insulated aerial cable is mainly used for city power distribution network, with simple construction, good mechanical, physical and electrical properties, safe enough. It also has good properties of resistance to tracking, surface laying distance, line length, voltage drop when comparing with bare wire, especially in reducing accident and ensuring safety of the body.

Main technical performance is negotiated with the Ministry of Energy Resources Wuhan High Voltage Research Institute in drawing up the enterprise standard. The cable will be well sold in Indonesia, Philippines, Thailand, etc., besides satisfying the needs of more than 20 provences and cities.

The product is used for electrical power transmission and distribution systems, operating at rated voltage of 1kV、10kV、35kV and below.

- Manufacturing Standard:

The standard for the product is GBl2527-90、GBl4049-93、SD237-87

2.  Application Characteristics:

    - Allowing operating temperature in long-term:

PVC insulated cable shall be 70℃；

PE insulated cable shall be 70℃；

XLPE insulated cable shall be 90℃.

    - The maximum short-circuit temperature (within 5s):

PVC insulated cable shall be 160℃；

PE insulated cable shall be 130℃；

XLPE insulated cable shall be 250℃.

    - The ambient temperature during operating shall not be lower than -20℃.

    - The ambient temperature during operating shall be -40℃—40℃，relative humidity in rainy reason shall not be less than 90％.

    - The bending radius of cable:

Rated voltage of 0.6/1kV and below:

Outer diameter D<25mm，bending radius shall not be less than 4D.

Outer diameter D≥25mm，bending radius shall not be less than 6D.

Rated voltage of 10kV,35kV:

Single core cable:  20(D+d)±5％mm

Multi-core cable:  15(D+d)±5％mm

Where:  D-the actual outer diameter of the cable   mm

d—the actual outer diameter of the conductor   mm

3.  Type and Specification of Cable:

- Refer to Table 1,2 about the type of cable.

- Refer to Table 3 about the specification of cable.

# Table 1

| Rated Voltage | Type |  | Name | Range of Application |
| --- | --- | --- | --- | --- |
|  | GB12527-90 | SD237-87 |  |  |
| 0.6/1 | JKV | JV | Cu. core PVC insulated aerial cable | Aerial permanent installation leading-in cable, etc |
|  | JKLV | JLV | Al. core PVC insulated aerial cable | Aerial permanent installation leading |
|  | JKY | JY | Cu. core PE insulated aerial cable | Aerial permanent installation leading |
|  | JKLY | JLY | Al. core PE insulated aerial cable | Aerial permanent installation leading |
|  | JKYJ | JYJ | Cu. core XLPE insulated aerial cable | Aerial permanent installation leading |
|  | JKLYJ | JLYJ | Al. core XLPE insulated aerial cable | Aerial permanent installation leading |

# Table 2

| Rated Voltage | Type |  | Name |
| --- | --- | --- | --- |
|  | GB14049-90 | Q/09TDL004 |  |
| 10 35 | JKYJ | JYJ | Cu. core XLPE insulated aerial cable |
|  | JKLYJ | JLYJ | Al. core XLPE insulated aerial cable |
|  | JKY | JY | Cu. core PE insulated aerial cable |
|  | JKLY | JLY | Al. core PE insulated aerial cable |
|  |  | JKGLYJ | Aluminum conductor steel-reinforced XLPE insulated aerial cable |
|  |  | JKGLY | Aluminum conductor steel-reinforced PE insulated aerial cable |

# Table 3

| Rated Voltage | No. of Cores | Nominal Cross-section |
| --- | --- | --- |
| 10 | 1、3 | 10—300 |
| 35 | 1 | 50—300 |
| 0.6/1 | 1、2、3、4 | 16—240 |

4. Main technical specification of the cable:

- Conductor of the cable is compacted round stranded conductor. It should be in accordance with the regulations in GB/T3956-1997.

- Cable insulation material is black weatherability PVC, PE, XLPE insulating material.

- Construction and technical performance of the cable are as Table 4, 5 and 6.

- The finished cable should withstand the A.C. voltage test:

Cable of rated voltage 0.6/1kV and below should withstand the water immersion voltage withstand test of 3500V, 1min.

A.C. voltage test of the cable(rated voltage 10kV、35kV) is as Table7.

- Partial discharge test should be done for rated voltage 10kV and 35kV cable with outer screen. The test must be done on the finished cable which is putted in water and use A.C. voltage. Testing voltage should be 9kV for 10kV cable and 31.5kV for 35kV cable. The magnitude of partial discharge should not be more than 20pc.

- There must be clear continuous mark of works, type and voltage class on cable surface.

5.  Referential Current Capacity:

Referential current capacity in air (ambient temperature 30℃). See Table 8.

Rating factor of temperature. See Table 9.

6.Delivery Length:

The delivery length of the cable shall not be less than 300m. With the amount of short strands being 10% of the total length, the length for each short strand is not less than times of 50m. The delivery  length can be decided through negotiation by both parties.

- Writing of type, size, number to order:

Please indicate the type, voltage class, nominal cross-section, product standard and numbers.

For example, if you order 10km copper core weatherability XLPE insulated aerial cable, normal cross-section is 185mm2, rated voltage is 10kV indicate as:

JKYJ 10kV 1×185mm2  10km  GBl4049-93。

Table 4

| Rated Voltage kV | Conductor Core |  |  | Nominal Thickness of Insualtion mm | Max. Overall Diameter mm | D.C. Resistance at 20℃ (no more than) |  | Min. Insulation Resistance at 70℃ MΩ·km | Calculated Breaking Load KN |  | Referential Weight of Cable kg／km |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Nominal Cross- section mm2 | Construction(No./mm) | Diameter mm |  |  | Cu. Core | Al. Core |  | Cu. Core | Al. Core | Cu. Core | Al. Core |
| 0.6/1 | 16 | 7/1.80 | 4.60 | 1.0 | 7.1 | 1.15 | 1.91 | 0.0050 | 5.120 | 2.556 | 160 | 67 |
|  | 25 | 7/2.25 | 6.0 | 1.2 | 8.9 | 0.727 | 1.20 | 0.0050 | 8.135 | 3.920 | 267 | 110 |
|  | 35 | 7/2.62 | 7.0 | 1.2 | 10.0 | 0.524 | 0.868 | 0.0045 | 11.139 | 5.184 | 355 | 140 |
|  | 50 | 19/1.89 | 8.30 | 1.4 | 11.7 | 0.387 | 0.641 | 0.0040 | 15.430 | 7.137 | 497 | 196 |
|  | 70 | 19/2.25 | 10.0 | 1.4 | 13.5 | 0.268 | 0.443 | 0.0035 | 22.081 | 9.855 | 703 | 266 |
|  | 95 | 19/2.62 | 11.6 | 1.6 | 15.8 | 0.193 | 0.320 | 0.0035 | 30.234 | 13.005 | 946 | 357 |
|  | 120 | 37/2.25 | 13.0 | 1.6 | 17.5 | 0.153 | 0.253 | 0.0032 | 38.791 | 17.478 | 1172 | 432 |
|  | 150 | 37/2.36 | 14.6 | 1.8 | 19.4 | 0.124 | 0.2C6 | 0.0032 | 47.295 | 20.979 | 1478 | 546 |
|  | 185 | 37/2.62 | 16.2 | 2.0 | 21.7 | 0.099 | 0.164 | 0.0092 | 58.878 | 25.596 | 1821 | 673 |
|  | 240 | 62/2.36 | 18.4 | 22 | 24.7 | 0.075 | 0.125 | 0.0032 | 69.765 | 32.634 | 2341 | 860 |

Table 5

| Nominal Cross- section of Conductor mm2 | Min. Individual Wire No. | Nominal Diameter of Conductormm | Min. Thickness of Conductor Screen (Approx.) mm |  | Nominal Thickness of Insulation mm |  |  | Nominal Thickness of Insulation Screen |  | Conductor Resistance at 20℃ (no more than) MΩ·km |  |  |  | Conductor Breaking Load (no less than) KN |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | 10 kV | 35 kV | Hard Cu. Core | Anneal Cu. Core | Al. Core | Aluminum Alloy Core | Hard Cu. Core | Al. Core | Aluminum Alloy Core |
|  |  |  |  |  | 10 kV |  | 35 kV |  |  |  |  |  |  |  |  |  |
|  |  |  | 10 kV | 35 kV | Thin Insulation | Insulation |  |  |  |  |  |  |  |  |  |  |
| 16 25 35 50 70 95 120 150 185 240 300 | 6 6 6 6 12 15 18 18 30 34 34 | 4.8 6.0 7.0 8.3 10.0 11.6 13.0 14.6 16.2 18.4 20.6 | 0.5 0.5 0.5 0.5 0.5 0.6 0.6 0.6 0.6 0.6 0.6 | - - - 0.8 0.8 0.8 0.8 0.8 0.8 0.8 0.8 | - 2.5 2.5 2.5 2.5 2.5 2.5 2.5 2.5 2.5 2.5 | 3.4 3.4 3.4 3.4 3.4 3.4 3.4 3.4 3.4 3.4 3.4 | - - - 9.3 9.3 9.3 9.3 9.3 9.3 9.3 9.3 | - 1.0 1.0 1.0 1.0 1.0 1.0 1.0 1.0 1.0 1.0 | - - - 1.5 1.5 1.5 1.5 1.5 1.5 1.5 1.5 | - 0.749 0.540 0.399 0.276 0.199 0.158 0.128 0.1021 0.0777 0.0619 | 1.150 0.727 0.524 0.387 0.268 0.193 0.153 - - - - | 1.910 1.200 0.868 0.641 0.443 0.320 0.253 0.206 0.164 0.125 0.100 | - 1.393 1.007 0.744 0.514 0.371 0.294 0.239 0.190 0.145 0.110 | - 8465 11731 1650.2 23461 31759 39911 49505 61846 79823 99788 | - 3762 5177 7011 10354 13727 17339 21033 26732 34679 43349 | - 6284 8800 12569 17596 23880 30164 37706 46503 60329 75411 |

Main technical performance of the Aluminum Conductor Steel-reinforced: Table 6

| Nominal Cross-section Al./St. mm2 | 25/4 | 35/6 | 50/8 | 70/10 | 95/15 | 120/20 | 15/20 | 185/25 | 240/30 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Construction (No./dia.) Al./St. mm | 6/2.45 | 6/2.89 | 6/3.40 | 24/2.02 | 26/2.28 | 26/2.54 | 24/2.89 | 24/3.32 | 24/3.76 |
|  | 1/2.32 | 1/2.72 | 1/3.20 | 1/3.80 | 7/1.67 | 7/1.85 | 7/1.85 | 7/2.10 | 7/2.40 |
| Diameter mm | 6.82 | 8.00 | 9.40 | 11.20 | 13.20 | 14.80 | 16.25 | 18.15 | 21.20 |
| Calculated Breaking Load | 8826 | 11999 | 16027 | 22221 | 33250 | 38950 | 44299 | 56449 | 68418 |

Table 7

| Rated Voltage kV | Nominal Thickness of Insulation mm | Test Condition | A.C. Testing Voltage kV | Sustaining Time min | Test Result |
| --- | --- | --- | --- | --- | --- |
| 10 | 2.5 | In Water at ambient temperature | 12 | 1 | No breakdown |
|  | 3.4 |  | 18 |  |  |
| 35 | 9.3 |  | 63 |  |  |

- Referential Current Capacity:

- a. Referential current rating in air(ambient temperature 30℃). See Table 8.

Table 8

| Voltage kV Material Conductor Cross-section mm2 | 0．6／1 |  |  |  |  |  | 10 |  | 35 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Cu. |  |  | Al. |  |  | Cu. | Al. | Cu. | Al. |
|  | PVC | PE | XLPE | PVC | PE | XLPE | XLPE | XLPE | XLPE | XLPE |
| 16 | 102 | 104 | 134 | 79 | 81 | 104 | - | - | - | - |
| 25 | 138 | 142 | 182 | 107 | 111 | 141 | 158 | 122 | - | - |
| 35 | 170 | 175 | 224 | 132 | 136 | 174 | 192 | 149 | - | - |
| 50 | 209 | 216 | 277 | 162 | 168 | 215 | 232 | 180 | 2C6 | 160 |
| 70 | 266 | 275 | 352 | 207 | 214 | 274 | 291 | 226 | 253 | 195 |
| 95 | 332 | 344 | 440 | 257 | 267 | 341 | 357 | 276 | 310 | 243 |
| 120 | 384 | 400 | 513 | 299 | 311 | 398 | 413 | 320 | 355 | 285 |
| 150 | 448 | 459 | 586 | 342 | 356 | 454 | 473 | 366 | 416 | 322 |
| 185 | 515 | 536 | 684 | 399 | 416 | 531 | 545 | 423 | 462 | 355 |
| 240 | 615 | 641 | 820 | 476 | 497 | 635 | 647 | 503 | 537 | 417 |

b. Rating Factor of Temperature                          Table 9

| Material | Voltage Class kV | Conductor Temperature ℃ | Rating factor of current rating for ambient temperature （℃） K |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | -5 | 0 | +5 | +10 | +15 | +20 | +30 | +35 | +40 | +45 |
| PVC PE | 0.6/1 | 70 | 1.37 | 1.27 | 1.23 | 1.18 | 1.17 | 1.12 | 1 | 0.94 | 0.87 | 0.70 |
| XLPE | 0.6/1 | 90 | 1.26 | 1.23 | 1.19 | 1.16 | 1.12 | 1.06 | 1 | 0.96 | 0.91 | 0.87 |
| XLPE | 10/35 | 90 | - | 1.41 | 1.43 | 1.37 | 1.32 | 1.26 | 1.14 | 1.07 | 1 |  |

Weatherability Insulated Parallel House Service Wire

The product is insulated with weatherability PVC, PE and XLPE. It has good properties of insulation and weather resistance. Two insulated cores are parallel and have isolation tape between them. The middle tape is easy to break when laying joints. It is used for electrical power transmission and distribution systems of power lighting and family electrical equipments, operating at rated voltage of 0.6/1kV and below. It is the idea replacement of rubber insulated wire.

- Manufacturing Standard:

The standard for the product is GB12527-90, SD237-87 Aerial Insulated Wire and Cable of Rated Voltage 1kV and Below.

- Application Requirements:

  - Rated voltage of the cable (U0/U) is 0.6/1kV.

  - Operating temperature of the conductor in long-term is:

XLPE：90℃；PE：80℃；PVC：70℃.

C.  The min. bending radius of the finished cable is 12 times (thickness of the wire +d). d:diameter of the conductor.

d. The ambient temperature of the wire should not be less than -20℃ during installation.

- Type and Specification:

Refer to Table 10 about the type and specification of cable.

Table 10

| Type | Name | Specification mm2 |
| --- | --- | --- |
| JKYB （JKLYB） | Cu. (Al.) conductor weatherability PE insulated parallel house service wire | 2×4 2×6 2×10 2×16 |
| JKVB （JKLVB） | Cu. (Al.) conductor weatherability PVC insulated parallel house service wire | 2×4 2×6 2×10 2×16 |
| JKYJB （JKLYJB） | Cu. (Al.) conductor weatherability XLPE insulated parallel house service wire | 2×4 2×6 2×10 2×16 |

- Construction of Cable

5. Main Technical Index:

| Item | Properties |
| --- | --- |
| Resistivity of Conductor at 20℃ (no more than) Cu. Al. | 0.017241Ω·mm2/m 0.028264Ω·mm2/m |
| Delivery Power Frequency Voltage Test | 3.5kV/1min |
| Insulation Resistance at Max. Operating Temperature (no less than) | XLPE、PE ：0.67MΩ·km PVC：0.0067 MΩ·km |

- Delivery Length and Notes to Order:

  - Delivery length shall not be less than 100m with the amount of short wire being 10% of the total length, the length for each short wire is not less than 20m.

  - Please indicate the type, size, number and standard when ordering the wire.

For example: If you order copper conductor weatherability PE insulated parallel house service wire, 2×6 mm2, 2km.

Please indicate as:

JKYB 2×6 mm2  2km  SD237-87